## BACnet Objekte Selbstauskunft
Gemäß DIN EN ISO 16484-5, Ausgabe:2012-11: Systeme der Gebäudeautomation Datenkommunikationsprotokoll und ANSI/ASHRAE-Standard 135-2012 | [7 empty] | AS | Anforderung | MBE
BACnet Protocol Version/Revision berücksichtigt: |  |  |  |  | BACnet Protocol |  |  | Universität Bonn
BACnet Protocol Version: 1 |  |  |  |  | Version/Revision angewandt: |  |  | UNI_BN2016
BACnet Protocol Revision: 17
BACnet Objekt |  |  |  |  | Protokol Informationen |  |  | Stand: | 2016-08-08
Objekttyp (OBJECT TYPE) |  | Property-Kennzeichnung (PROPERTY IDENTIFIER) |  | BACnet Standard CONF. CODE | Quelle ASHRAE | Protocol Version | Protocol Revision | UNI_BN 2016 |  | UNI_BN 2016
Objektkürzel / (Objektnummer gemäß Norm) | Objektbeschreibung | Nr. | Beschreibung (original) |  |  | 1 | 17 | AS | Bemerkungen | MBE
Datum PICS:
Vendor Name:
Produkt Name:
Produkt Modell Nummer:
Applikations Software Version:
Firmware Revision:
BACnet Protocol Revision:
AI (0) | Analog Input | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Analog Input | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 85 | Present_Value | R1 | 135-2001 | 1 | 2 | R1 | R1=W wenn Out_Of_Service = WAHR | M
| Analog Input | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Analog Input | 31 | Device_Type | O | 135-2001 | 1 | 2 | R | optional | M
| Analog Input | 111 | Status_Flags | R | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 103 | Reliability | O | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 81 | Out_Of_Service | R | 135-2001 | 1 | 2 | W |  | M
| Analog Input | 118 | Update_Interval | O | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 117 | Units | R | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 69 | Min_Pres_Value | O | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 65 | Max_Pres_Value | O | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 106 | Resolution | O | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 22 | COV_Increment | O2 | 135-2001 | 1 | 2 | W |  | M
| Analog Input | 113 | Time_Delay | O3,5 | 135-2001 | 1 | 2 | W |  | M
| Analog Input | 17 | Notification_Class | O3,5 | 135-2001 | 1 | 2 | W |  | M
| Analog Input | 45 | High_Limit | O3,5 | 135-2001 | 1 | 2 | W |  | M
| Analog Input | 59 | Low_Limit | O3,5 | 135-2001 | 1 | 2 | W |  | M
| Analog Input | 25 | Deadband | O3,5 | 135-2001 | 1 | 2 | W |  | M
| Analog Input | 52 | Limit_Enable | O3,5 | 135-2001 | 1 | 2 | W |  | M
| Analog Input | 35 | Event_Enable | O3,5 | 135-2001 | 1 | 2 | W |  | M
| Analog Input | 0 | Acked_Transitions | O3,5 | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 72 | Notify_Type | O3,5 | 135-2001 | 1 | 2 | R |  | M
| Analog Input | 130 | Event_Time_Stamps | O3,5 | 135-2001 | 1 | 2 | R |  | P
| Analog Input | 351 | Event_Message_Texts | O4,5 | 135-2008 Add z | 1 | 11 | R |  | P
| Analog Input | 352 | Event_Message_Texts_Config | O5 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Input | 353 | Event_Detection_Enable | O3,5 | 135-2010 Add af | 1 | 13 | R |  | P
| Analog Input | 355 | Event_Algorithm_Inhibit_Ref | O5 | 135-2010 Add af | 1 | 13 | R |  | P
| Analog Input | 354 | Event_Algorithm_Inhibit | O5,6 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Input | 356 | Time_Delay_Normal | O5 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Input | 357 | Reliability_Evaluation_Inhibit | O7 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Input | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Analog Input | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
AO (1) | Analog Output | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Analog Output | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 85 | Present_Value | W | 135-2001 | 1 | 2 | W |  | M
| Analog Output | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Analog Output | 31 | Device_Type | O | 135-2001 | 1 | 2 | R | optional | M
| Analog Output | 111 | Status_Flags | R | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 103 | Reliability | O | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 81 | Out_Of_Service | R | 135-2001 | 1 | 2 | R |  | M
| Analog Output | 117 | Units | R | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 69 | Min_Pres_Value | O | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 65 | Max_Pres_Value | O | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 106 | Resolution | O | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 87 | Priority_Array | R | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 104 | Relinquish_Default | R | 135-2001 | 1 | 2 | R |  | M
| Analog Output | 22 | COV_Increment | O1 | 135-2001 | 1 | 2 | W |  | M
| Analog Output | 113 | Time_Delay | O2,4 | 135-2001 | 1 | 2 | W |  | M
| Analog Output | 17 | Notification_Class | O2,4 | 135-2001 | 1 | 2 | W |  | M
| Analog Output | 45 | High_Limit | O2,4 | 135-2001 | 1 | 2 | W |  | M
| Analog Output | 59 | Low_Limit | O2,4 | 135-2001 | 1 | 2 | W |  | M
| Analog Output | 25 | Deadband | O2,4 | 135-2001 | 1 | 2 | W |  | M
| Analog Output | 52 | Limit_Enable | O2,4 | 135-2001 | 1 | 2 | W |  | M
| Analog Output | 35 | Event_Enable | O2,4 | 135-2001 | 1 | 2 | W |  | M
| Analog Output | 0 | Acked_Transitions | O2,4 | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 72 | Notify_Type | O2,4 | 135-2001 | 1 | 2 | R |  | M
| Analog Output | 130 | Event_Time_Stamps | O2,4 | 135-2001 | 1 | 2 | R |  | P
| Analog Output | 351 | Event_Message_Texts | O3,4 | 135-2008 Add z | 1 | 11 | R |  | P
| Analog Output | 352 | Event_Message_Texts_Config | O4 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Output | 353 | Event_Detection_Enable | O2,4 | 135-2010 Add af | 1 | 13 | R |  | P
| Analog Output | 355 | Event_Algorithm_Inhibit_Ref | O4 | 135-2010 Add af | 1 | 13 | R |  | P
| Analog Output | 354 | Event_Algorithm_Inhibit | O4,5 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Output | 356 | Time_Delay_Normal | O4 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Output | 357 | Reliability_Evaluation_Inhibit | O6 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Output | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Analog Output | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
AV (2) | Analog Value | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Analog Value | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Analog Value | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Analog Value | 85 | Present_Value | R4 | 135-2001 | 1 | 2 | R4 |  | M
| Analog Value | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Analog Value | 111 | Status_Flags | R | 135-2001 | 1 | 2 | R |  | P
| Analog Value | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Analog Value | 103 | Reliability | O | 135-2001 | 1 | 2 | R |  | P
| Analog Value | 81 | Out_Of_Service | R | 135-2001 | 1 | 2 | R |  | M
| Analog Value | 117 | Units | R | 135-2001 | 1 | 2 | R |  | P
| Analog Value | 87 | Priority_Array | O1 | 135-2001 | 1 | 2 | R |  | P
| Analog Value | 104 | Relinquish_Default | O1 | 135-2001 | 1 | 2 | W |  | M
| Analog Value | 22 | COV_Increment | O2 | 135-2001 | 1 | 2 | W |  | M
| Analog Value | 113 | Time_Delay | O3,6 | 135-2001 | 1 | 2 | W |  | M
| Analog Value | 17 | Notification_Class | O3,6 | 135-2001 | 1 | 2 | W |  | M
| Analog Value | 45 | High_Limit | O3,6 | 135-2001 | 1 | 2 | W |  | M
| Analog Value | 59 | Low_Limit | O3,6 | 135-2001 | 1 | 2 | W |  | M
| Analog Value | 25 | Deadband | O3,6 | 135-2001 | 1 | 2 | W |  | M
| Analog Value | 52 | Limit_Enable | O3,6 | 135-2001 | 1 | 2 | W |  | M
| Analog Value | 35 | Event_Enable | O3,6 | 135-2001 | 1 | 2 | W |  | M
| Analog Value | 0 | Acked_Transitions | O3,6 | 135-2001 | 1 | 2 | R |  | P
| Analog Value | 72 | Notify_Type | O3,6 | 135-2001 | 1 | 2 | R |  | M
| Analog Value | 130 | Event_Time_Stamps | O3,6 | 135-2001 | 1 | 2 | R |  | P
| Analog Value | 351 | Event_Message_Texts | O5,6 | 135-2008 Add z | 1 | 11 | R |  | P
| Analog Value | 352 | Event_Message_Texts_Config | O6 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Value | 353 | Event_Detection_Enable | O3,6 | 135-2010 Add af | 1 | 13 | R |  | P
| Analog Value | 355 | Event_Algorithm_Inhibit_Ref | O6 | 135-2010 Add af | 1 | 13 | R |  | P
| Analog Value | 354 | Event_Algorithm_Inhibit | O6,7 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Value | 356 | Time_Delay_Normal | O6 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Value | 357 | Reliability_Evaluation_Inhibit | O8 | 135-2010 Add af | 1 | 13 | W |  | M
| Analog Value | 69 | Min_Pres_Value | O | 135-2010 Add ao | 1 | 14 | O |  | P
| Analog Value | 65 | Max_Pres_Value | O | 135-2010 Add ao | 1 | 14 | O |  | P
| Analog Value | 106 | Resolution | O | 135-2010 Add ao | 1 | 14 | O |  | P
| Analog Value | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Analog Value | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
BI (3) | Binary Input | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Binary Input | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Binary Input | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Binary Input | 85 | Present_Value | R1 | 135-2001 | 1 | 2 | R1 | R1=W wenn Out_Of_Service = WAHR | M
| Binary Input | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Binary Input | 31 | Device_Type | O | 135-2001 | 1 | 2 | R | optional | M
| Binary Input | 111 | Status_Flags | R | 135-2001 | 1 | 2 | R |  | P
| Binary Input | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Binary Input | 103 | Reliability | O | 135-2001 | 1 | 2 | R |  | P
| Binary Input | 81 | Out_Of_Service | R | 135-2001 | 1 | 2 | W |  | M
| Binary Input | 84 | Polarity | R | 135-2001 | 1 | 2 | R |  | M
| Binary Input | 46 | Inactive_Text | O2 | 135-2001 | 1 | 2 | R |  | M
| Binary Input | 4 | Active_Text | O2 | 135-2001 | 1 | 2 | R |  | M
| Binary Input | 16 | Change_Of_State_Time | O3 | 135-2001 | 1 | 2 | R |  | P
| Binary Input | 15 | Change_Of_State_Count | O3 | 135-2001 | 1 | 2 | W |  | M
| Binary Input | 115 | Time_Of_State_Count_Reset | O3 | 135-2001 | 1 | 2 | R |  | P
| Binary Input | 33 | Elapsed_Active_Time | O4 | 135-2001 | 1 | 2 | W | = zusätzliche EE-Objekte für GW! | M
| Binary Input | 114 | Time_Of_Active_Time_Reset | O4 | 135-2001 | 1 | 2 | R |  | P
| Binary Input | 113 | Time_Delay | O5,7 | 135-2001 | 1 | 2 | W |  | M
| Binary Input | 17 | Notification_Class | O5,7 | 135-2001 | 1 | 2 | W |  | M
| Binary Input | 6 | Alarm_Value | O5,7 | 135-2001 | 1 | 2 | R |  | M
| Binary Input | 35 | Event_Enable | O5,7 | 135-2001 | 1 | 2 | W |  | M
| Binary Input | 0 | Acked_Transitions | O5,7 | 135-2001 | 1 | 2 | R |  | P
| Binary Input | 72 | Notify_Type | O5,7 | 135-2001 | 1 | 2 | R |  | M
| Binary Input | 130 | Event_Time_Stamps | O5,7 | 135-2001 | 1 | 2 | R |  | P
| Binary Input | 351 | Event_Message_Texts | O6,7 | 135-2008 Add z | 1 | 11 | R |  | P
| Binary Input | 352 | Event_Message_Texts_Config | O7 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Input | 353 | Event_Detection_Enable | O5,7 | 135-2010 Add af | 1 | 13 | R |  | P
| Binary Input | 355 | Event_Algorithm_Inhibit_Ref | O7 | 135-2010 Add af | 1 | 13 | R |  | P
| Binary Input | 354 | Event_Algorithm_Inhibit | O7,8 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Input | 356 | Time_Delay_Normal | O7 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Input | 357 | Reliability_Evaluation_Inhibit | O9 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Input | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Binary Input | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
BO (4) | Binary Output | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Binary Output | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 85 | Present_Value | W | 135-2001 | 1 | 2 | W |  | M
| Binary Output | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Binary Output | 31 | Device_Type | O | 135-2001 | 1 | 2 | R | optional | M
| Binary Output | 111 | Status_Flags | R | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 103 | Reliability | O | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 81 | Out_Of_Service | R | 135-2001 | 1 | 2 | R |  | M
| Binary Output | 84 | Polarity | R | 135-2001 | 1 | 2 | R |  | M
| Binary Output | 46 | Inactive_Text | O1 | 135-2001 | 1 | 2 | R |  | M
| Binary Output | 4 | Active_Text | O1 | 135-2001 | 1 | 2 | R |  | M
| Binary Output | 16 | Change_Of_State_Time | O2 | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 15 | Change_Of_State_Count | O2 | 135-2001 | 1 | 2 | W |  | M
| Binary Output | 115 | Time_Of_State_Count_Reset | O2 | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 33 | Elapsed_Active_Time | O3 | 135-2001 | 1 | 2 | W |  | M
| Binary Output | 114 | Time_Of_Active_Time_Reset | O3 | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 66 | Minimum_Off_Time | O | 135-2001 | 1 | 2 | W |  | M
| Binary Output | 67 | Minimum_On_Time | O | 135-2001 | 1 | 2 | W |  | M
| Binary Output | 87 | Priority_Array | R | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 104 | Relinquish_Default | R | 135-2001 | 1 | 2 | R |  | M
| Binary Output | 113 | Time_Delay | O4,6 | 135-2001 | 1 | 2 | W |  | M
| Binary Output | 17 | Notification_Class | O4,6 | 135-2001 | 1 | 2 | W |  | M
| Binary Output | 40 | Feedback_Value | O4 | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 35 | Event_Enable | O4,6 | 135-2001 | 1 | 2 | W |  | M
| Binary Output | 0 | Acked_Transitions | O4,6 | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 72 | Notify_Type | O4,6 | 135-2001 | 1 | 2 | R |  | M
| Binary Output | 130 | Event_Time_Stamps | O4,6 | 135-2001 | 1 | 2 | R |  | P
| Binary Output | 351 | Event_Message_Texts | O5,6 | 135-2008 Add z | 1 | 11 | R |  | P
| Binary Output | 352 | Event_Message_Texts_Config | O6 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Output | 353 | Event_Detection_Enable | O4,6 | 135-2010 Add af | 1 | 13 | R |  | P
| Binary Output | 355 | Event_Algorithm_Inhibit_Ref | O6 | 135-2010 Add af | 1 | 13 | R |  | P
| Binary Output | 354 | Event_Algorithm_Inhibit | O6,7 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Output | 356 | Time_Delay_Normal | O6 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Output | 357 | Reliability_Evaluation_Inhibit | O8 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Output | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Binary Output | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
BV (5) | Binary Value | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Binary Value | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Binary Value | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Binary Value | 85 | Present_Value | R1 | 135-2001 | 1 | 2 | R1 |  | M
| Binary Value | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Binary Value | 111 | Status_Flags | R | 135-2001 | 1 | 2 | R |  | P
| Binary Value | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Binary Value | 103 | Reliability | O | 135-2001 | 1 | 2 | R |  | P
| Binary Value | 81 | Out_Of_Service | R | 135-2001 | 1 | 2 | W |  | M
| Binary Value | 46 | Inactive_Text | O2 | 135-2001 | 1 | 2 | R |  | M
| Binary Value | 4 | Active_Text | O2 | 135-2001 | 1 | 2 | R |  | M
| Binary Value | 16 | Change_Of_State_Time | O3 | 135-2001 | 1 | 2 | R |  | P
| Binary Value | 15 | Change_Of_State_Count | O3 | 135-2001 | 1 | 2 | W |  | M
| Binary Value | 115 | Time_Of_State_Count_Reset | O3 | 135-2001 | 1 | 2 | R |  | P
| Binary Value | 33 | Elapsed_Active_Time | O4 | 135-2001 | 1 | 2 | W |  | M
| Binary Value | 114 | Time_Of_Active_Time_Reset | O4 | 135-2001 | 1 | 2 | R |  | P
| Binary Value | 66 | Minimum_Off_Time | O | 135-2001 | 1 | 2 | W |  | M
| Binary Value | 67 | Minimum_On_Time | O | 135-2001 | 1 | 2 | W |  | M
| Binary Value | 87 | Priority_Array | O5 | 135-2001 | 1 | 2 | R |  | P
| Binary Value | 104 | Relinquish_Default | O5 | 135-2001 | 1 | 2 | W |  | M
| Binary Value | 113 | Time_Delay | O6,8 | 135-2001 | 1 | 2 | W |  | M
| Binary Value | 17 | Notification_Class | O6,8 | 135-2001 | 1 | 2 | W |  | M
| Binary Value | 6 | Alarm_Value | O6,8 | 135-2001 | 1 | 2 | R |  | M
| Binary Value | 35 | Event_Enable | O6,8 | 135-2001 | 1 | 2 | W |  | M
| Binary Value | 0 | Acked_Transitions | O6,8 | 135-2001 | 1 | 2 | R |  | P
| Binary Value | 72 | Notify_Type | O6,8 | 135-2001 | 1 | 2 | R |  | M
| Binary Value | 130 | Event_Time_Stamps | O6,8 | 135-2001 | 1 | 2 | R |  | P
| Binary Value | 351 | Event_Message_Texts | O7,8 | 135-2008 Add z | 1 | 11 | R |  | P
| Binary Value | 352 | Event_Message_Texts_Config | O8 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Value | 353 | Event_Detection_Enable | O6,8 | 135-2010 Add af | 1 | 13 | R |  | P
| Binary Value | 355 | Event_Algorithm_Inhibit_Ref | O8 | 135-2010 Add af | 1 | 13 | R |  | P
| Binary Value | 354 | Event_Algorithm_Inhibit | O8,9 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Value | 356 | Time_Delay_Normal | O8 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Value | 357 | Reliability_Evaluation_Inhibit | O10 | 135-2010 Add af | 1 | 13 | W |  | M
| Binary Value | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Binary Value | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
CAL (6) | Calendar | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Calendar | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Calendar | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Calendar | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Calendar | 85 | Present_Value | R | 135-2001 | 1 | 2 | R |  | P
| Calendar | 23 | Date_List | R | 135-2001 | 1 | 2 | W |  | M
| Calendar | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Calendar | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
CMD (7) | Command | 75 | Object_Identifier | R | 135-2001 | 1 | 2
| Command | 77 | Object_Name | R | 135-2001 | 1 | 2
| Command | 79 | Object_Type | R | 135-2001 | 1 | 2
| Command | 28 | Description | O | 135-2001 | 1 | 2
| Command | 85 | Present_Value | W | 135-2001 | 1 | 2
| Command | 47 | In_Process | R | 135-2001 | 1 | 2
| Command | 9 | All_Writes_Successful | R | 135-2001 | 1 | 2
| Command | 2 | Action | R | 135-2001 | 1 | 2
| Command | 3 | Action_Text | O | 135-2001 | 1 | 2
| Command | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Command | 168 | Profile_Name | O | 135-2001 | 1 | 2
DEV (8) | DEVICE | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| DEVICE | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 112 | System_Status | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 121 | Vendor_Name | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 120 | Vendor_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 70 | Model_Name | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 44 | Firmware_Revision | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 12 | Application_Software_Version | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 58 | Location | O | 135-2001 | 1 | 2 | W |  | P
| DEVICE | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| DEVICE | 98 | Protocol_Version | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 139 | Protocol_Revision | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 97 | Protocol_Services_Supported | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 96 | Protocol_Object_Types_Supported | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 76 | Object_List | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 209 | Structured_Object_List | O | 135-2004 Add d | 1 | 5 | O |  | P
| DEVICE | 62 | Max_APDU_Length_Accepted | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 107 | Segmentation_Supported | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 167 | Max_Segments_Accepted | O1 | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 122 | VT_Classes_Supported | O2 | 135-2001 | 1 | 2 | O |  | P
| DEVICE | 5 | Active_VT_Sessions | O2 | 135-2001 | 1 | 2 | O |  | P
| DEVICE | 57 | Local_Time | O3,4,15 | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 56 | Local_Date | O3,4,15 | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 119 | UTC_Offset | O4 | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 24 | Daylight_Savings_Status | O4 | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 10 | APDU_Segment_Timeout | O1 | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 11 | APDU_Timeout | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 73 | Number_Of_APDU_Retries | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 54 | List_Of_Session_Keys | O | 135-2001entfällt ab 2010 | 1 | 2 | O |  | O
| DEVICE | 116 | Time_Synchronization_Recipients | O5 | 135-2001 | 1 | 2 | O |  | P
| DEVICE | 64 | Max_Master | O6 | 135-2001 | 1 | 2 | O |  | P
| DEVICE | 63 | Max_Info_Frames | O6 | 135-2001 | 1 | 2 | O |  | P
| DEVICE | 30 | Device_Address_Binding | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 155 | Database_Revision | R | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 154 | Configuration_Files | O7 | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 157 | Last_Restore_Time | O7 | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 153 | Backup_Failure_Timeout | O8 | 135-2001 | 1 | 2 | W |  | M
| DEVICE | 339 | Backup_Preparation_Time | O16 | 135-2008 Add n | 1 | 10 | R |  | P
| DEVICE | 341 | Restore_Preparation_Time | O16 | 135-2008 Add n | 1 | 10 | R |  | P
| DEVICE | 340 | Restore_Completion_Time | O16 | 135-2008 Add n | 1 | 10 | R |  | P
| DEVICE | 338 | Backup_And_Restore_State | O7 | 135-2008 Add n | 1 | 10 | R |  | P
| DEVICE | 152 | Active_COV_Subscriptions | O9 | 135-2001 | 1 | 2 | R |  | P
| DEVICE | 172 | Slave_Proxy_Enable | O10 | 135-2001 Add a | 1 | 4 | O |  | P
| DEVICE | 170 | Manual_Slave_Address_Binding | O10,12 | 135-2001 Add a | 1 | 4 | O |  | P
| DEVICE | 169 | Auto_Slave_Discovery | O10,11 | 135-2001 Add a | 1 | 4 | O |  | P
| DEVICE | 171 | Slave_Address_Binding | O10,12 | 135-2001 Add a | 1 | 4 | O |  | P
| DEVICE | 196 | Last_Restart_Reason | O13 | 135-2004 Add b | 1 | 7 | R |  | P
| DEVICE | 203 | Time_Of_Device_Restart | O13 | 135-2004 Add b | 1 | 7 | R |  | P
| DEVICE | 202 | Restart_Notification_Recipients | O17 | 135-2004 Add b | 1 | 7 | R |  | P
| DEVICE | 206 | UTC_Time_Synchronization_Recipients | O5 | 135-2004 Add b | 1 | 7 | O |  | P
| DEVICE | 204 | Time_Synchronization_Interval | O14 | 135-2004 Add b | 1 | 7 | O |  | P
| DEVICE | 193 | Align_Intervals | O14 | 135-2004 Add b | 1 | 7 | O |  | P
| DEVICE | 195 | Interval_Offset | O14 | 135-2004 Add b | 1 | 7 | O |  | P
| DEVICE | 372 | Serial_Number | O | 135-2010 Add ak | 1 | 14 | R |  | P
| DEVICE | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| DEVICE | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
EE (9) | Event Enrollment | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Event Enrollment | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Event Enrollment | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Event Enrollment | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Event Enrollment | 37 | Event_Type | R | 135-2001 | 1 | 2 | R |  | P
| Event Enrollment | 72 | Notify_Type | R | 135-2001 | 1 | 2 | R |  | M
| Event Enrollment | 83 | Event_Parameters | R | 135-2001 | 1 | 2 | R |  | P
| Event Enrollment | 78 | Object_Property_Reference | R | 135-2001 | 1 | 2 | R |  | P
| Event Enrollment | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Event Enrollment | 35 | Event_Enable | R | 135-2001 | 1 | 2 | R |  | P
| Event Enrollment | 0 | Acked_Transitions | R | 135-2001 | 1 | 2 | R |  | P
| Event Enrollment | 17 | Notification_Class | R | 135-2001 Add a | 1 | 4 | W |  | M
| Event Enrollment | 130 | Event_Time_Stamps | R | 135-2001 | 1 | 2 | R |  | P
| Event Enrollment | 351 | Event_Message_Texts | O1 | 135-2008 Add z | 1 | 11 | R |  | P
| Event Enrollment | 352 | Event_Message_Texts_Config | O | 135-2010 Add af | 1 | 13 | W |  | M
| Event Enrollment | 353 | Event_Detection_Enable | R | 135-2010 Add af | 1 | 13 | R |  | P
| Event Enrollment | 355 | Event_Algorithm_Inhibit_Ref | O | 135-2010 Add af | 1 | 13 | R |  | P
| Event Enrollment | 354 | Event_Algorithm_Inhibit | O2 | 135-2010 Add af | 1 | 13 | W |  | M
| Event Enrollment | 356 | Time_Delay_Normal | O | 135-2010 Add af | 1 | 13 | W |  | M
| Event Enrollment | 111 | Status_Flags | R | 135-2010 Add af | 1 | 13 | R |  | P
| Event Enrollment | 103 | Reliability | R | 135-2010 Add af | 1 | 13 | R |  | P
| Event Enrollment | 359 | Fault_Type | O3 | 135-2010 Add af | 1 | 13 | R |  | P
| Event Enrollment | 358 | Fault_Parameters | O3 | 135-2010 Add af | 1 | 13 | R |  | P
| Event Enrollment | 357 | Reliability_Evaluation_Inhibit | O | 135-2010 Add af | 1 | 13 | W |  | M
| Event Enrollment | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Event Enrollment | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
FIL (10) | File | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| File | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | P
| File | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| File | 28 | Description | O | 135-2001 | 1 | 2 | R* | muss nicht frei definierbar sein | M*
| File | 43 | File_Type | R | 135-2001 | 1 | 2 | R |  | P
| File | 42 | File_Size | R1 | 135-2001 | 1 | 2 | R1 |  | P
| File | 71 | Modification_Date | R | 135-2001 | 1 | 2 | R |  | P
| File | 13 | Archive | W | 135-2001 | 1 | 2 | W |  | M
| File | 99 | Read_Only | R | 135-2001 | 1 | 2 | R |  | P
| File | 41 | File_Access_Method | R | 135-2001 | 1 | 2 | R |  | P
| File | 141 | Record_Count | O2 | 135-2001 | 1 | 2 | O |  | P
| File | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| File | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
GRP (11) | Group | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Group | 77 | Object_Name | R | 135-2001 | 1 | 2 | R |  | M
| Group | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Group | 28 | Description | O | 135-2001 | 1 | 2 | W |  | M
| Group | 53 | List_Of_Group_Members | R | 135-2004 Add b | 1 | 7 | R |  | P
| Group | 85 | Present_Value | R | 135-2001 | 1 | 2 | R |  | P
| Group | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Group | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
LP (12) | Loop | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Loop | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 85 | Present_Value | R7 | 135-2001 | 1 | 2 | R |  | P
| Loop | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Loop | 111 | Status_Flags | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 103 | Reliability | O7 | 135-2001 | 1 | 2 | R |  | P
| Loop | 81 | Out_Of_Service | R | 135-2001 | 1 | 2 | R |  | M
| Loop | 118 | Update_Interval | O | 135-2001 | 1 | 2 | R |  | P
| Loop | 82 | Output_Units | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 60 | Manipulated_Variable_Reference | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 19 | Controlled_Variable_Reference | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 21 | Controlled_Variable_Value | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 20 | Controlled_Variable_Units | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 109 | Setpoint_Reference | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 108 | Setpoint | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 2 | Action | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 93 | Proportional_Constant | O1 | 135-2001 | 1 | 2 | W |  | M
| Loop | 94 | Proportional_Constant_Units | O1 | 135-2001 | 1 | 2 | R |  | P
| Loop | 49 | Integral_Constant | O2 | 135-2001 | 1 | 2 | W |  | M
| Loop | 50 | Integral_Constant_Units | O2 | 135-2001 | 1 | 2 | R |  | P
| Loop | 26 | Derivative_Constant | O3 | 135-2001 | 1 | 2 | W |  | M
| Loop | 27 | Derivative_Constant_Units | O3 | 135-2001 | 1 | 2 | R |  | P
| Loop | 14 | Bias | O | 135-2001 | 1 | 2 | R |  | P
| Loop | 61 | Maximum_Output | O | 135-2001 | 1 | 2 | W |  | M
| Loop | 68 | Minimum_Output | O | 135-2001 | 1 | 2 | W |  | M
| Loop | 88 | Priority_For_Writing | R | 135-2001 | 1 | 2 | R |  | P
| Loop | 22 | COV_Increment | O4 | 135-2001 | 1 | 2 | W |  | M
| Loop | 113 | Time_Delay | O5,8 | 135-2001 | 1 | 2 | W |  | M
| Loop | 17 | Notification_Class | O5,8 | 135-2001 | 1 | 2 | W |  | M
| Loop | 34 | Error_Limit | O5,8 | 135-2001 | 1 | 2 | W |  | M
| Loop | 25 | Deadband | O5,8 | 135-2004 Add m | 1 | 7 | W |  | M
| Loop | 35 | Event_Enable | O5,8 | 135-2001 | 1 | 2 | W |  | M
| Loop | 0 | Acked_Transitions | O5,8 | 135-2001 | 1 | 2 | R |  | P
| Loop | 72 | Notify_Type | O5,8 | 135-2001 | 1 | 2 | R |  | M
| Loop | 130 | Event_Time_Stamps | O5,8 | 135-2001 | 1 | 2 | R |  | P
| Loop | 351 | Event_Message_Texts | O6,8 | 135-2008 Add z | 1 | 11 | R |  | P
| Loop | 352 | Event_Message_Texts_Config | O8 | 135-2010 Add af | 1 | 13 | W |  | M
| Loop | 353 | Event_Detection_Enable | O5,8 | 135-2010 Add af | 1 | 13 | R |  | P
| Loop | 355 | Event_Algorithm_Inhibit_Ref | O8 | 135-2010 Add af | 1 | 13 | R |  | P
| Loop | 354 | Event_Algorithm_Inhibit | O8,9 | 135-2010 Add af | 1 | 13 | W |  | M
| Loop | 356 | Time_Delay_Normal | O8 | 135-2010 Add af | 1 | 13 | W |  | M
| Loop | 357 | Reliability_Evaluation_Inhibit | O10 | 135-2010 Add af | 1 | 13 | W |  | M
| Loop | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Loop | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
MI (13) | Multi-state Input | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Input | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Multi-state Input | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Input | 85 | Present_Value | R1 | 135-2001 | 1 | 2 | R1 | R1=W wenn Out_Of_Service = WAHR | M
| Multi-state Input | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Multi-state Input | 31 | Device_Type | O | 135-2001 | 1 | 2 | R | optional | M
| Multi-state Input | 111 | Status_Flags | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Input | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Input | 103 | Reliability | O | 135-2001 | 1 | 2 | R |  | P
| Multi-state Input | 81 | Out_Of_Service | R | 135-2001 | 1 | 2 | R |  | M
| Multi-state Input | 74 | Number_Of_States | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Input | 110 | State_Text | O | 135-2001 | 1 | 2 | R |  | P
| Multi-state Input | 113 | Time_Delay | O3,5 | 135-2001 | 1 | 2 | W |  | M
| Multi-state Input | 17 | Notification_Class | O3,5 | 135-2001 | 1 | 2 | W |  | M
| Multi-state Input | 7 | Alarm_Values | O3,5 | 135-2001 | 1 | 2 | R |  | M
| Multi-state Input | 39 | Fault_Values | O7 | 135-2001 | 1 | 2 | R |  | P
| Multi-state Input | 35 | Event_Enable | O3,5 | 135-2001 | 1 | 2 | W |  | M
| Multi-state Input | 0 | Acked_Transitions | O3,5 | 135-2001 | 1 | 2 | R |  | P
| Multi-state Input | 72 | Notify_Type | O3,5 | 135-2001 | 1 | 2 | R |  | M
| Multi-state Input | 130 | Event_Time_Stamps | O3,5 | 135-2001 | 1 | 2 | R |  | P
| Multi-state Input | 351 | Event_Message_Texts | O4,5 | 135-2008 Add z | 1 | 11 | R |  | P
| Multi-state Input | 352 | Event_Message_Texts_Config | O5 | 135-2010 Add af | 1 | 13 | W |  | M
| Multi-state Input | 353 | Event_Detection_Enable | O3,5 | 135-2010 Add af | 1 | 13 | R |  | P
| Multi-state Input | 355 | Event_Algorithm_Inhibit_Ref | O5 | 135-2010 Add af | 1 | 13 | R |  | P
| Multi-state Input | 354 | Event_Algorithm_Inhibit | O5,6 | 135-2010 Add af | 1 | 13 | W |  | M
| Multi-state Input | 356 | Time_Delay_Normal | O5 | 135-2010 Add af | 1 | 13 | W |  | M
| Multi-state Input | 357 | Reliability_Evaluation_Inhibit | O7 | 135-2010 Add af | 1 | 13 | W |  | M
| Multi-state Input | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Multi-state Input | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
MO (14) | Multi-state Output | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Output | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Multi-state Output | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Output | 85 | Present_Value | W | 135-2001 | 1 | 2 | W |  | M
| Multi-state Output | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Multi-state Output | 31 | Device_Type | O | 135-2001 | 1 | 2 | R | optional | M
| Multi-state Output | 111 | Status_Flags | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Output | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Output | 103 | Reliability | O | 135-2001 | 1 | 2 | R |  | P
| Multi-state Output | 81 | Out_Of_Service | R | 135-2001 | 1 | 2 | R |  | M
| Multi-state Output | 74 | Number_Of_States | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Output | 110 | State_Text | O | 135-2001 | 1 | 2 | R |  | P
| Multi-state Output | 87 | Priority_Array | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Output | 104 | Relinquish_Default | R | 135-2001 | 1 | 2 | R |  | M
| Multi-state Output | 113 | Time_Delay | O1,3 | 135-2001 | 1 | 2 | W |  | M
| Multi-state Output | 17 | Notification_Class | O1,3 | 135-2001 | 1 | 2 | W |  | M
| Multi-state Output | 40 | Feedback_Value | O1 | 135-2001 | 1 | 2 | R |  | P
| Multi-state Output | 35 | Event_Enable | O1,3 | 135-2001 | 1 | 2 | W |  | M
| Multi-state Output | 0 | Acked_Transitions | O1,3 | 135-2001 | 1 | 2 | R |  | P
| Multi-state Output | 72 | Notify_Type | O1,3 | 135-2001 | 1 | 2 | R |  | M
| Multi-state Output | 130 | Event_Time_Stamps | O1,3 | 135-2001 | 1 | 2 | R |  | P
| Multi-state Output | 351 | Event_Message_Texts | O2,3 | 135-2008 Add z | 1 | 11 | R |  | P
| Multi-state Output | 352 | Event_Message_Texts_Config | O3 | 135-2010 Add af | 1 | 13 | R |  | M
| Multi-state Output | 353 | Event_Detection_Enable | O1,3 | 135-2010 Add af | 1 | 13 | W |  | P
| Multi-state Output | 355 | Event_Algorithm_Inhibit_Ref | O3 | 135-2010 Add af | 1 | 13 | R |  | P
| Multi-state Output | 354 | Event_Algorithm_Inhibit | O3,4 | 135-2010 Add af | 1 | 13 | R |  | M
| Multi-state Output | 356 | Time_Delay_Normal | O3 | 135-2010 Add af | 1 | 13 | W |  | M
| Multi-state Output | 357 | Reliability_Evaluation_Inhibit | O5 | 135-2010 Add af | 1 | 13 | W |  | M
| Multi-state Output | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | W |  | P
| Multi-state Output | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
NC (15) | Notification Class | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Notification Class | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Notification Class | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Notification Class | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Notification Class | 17 | Notification_Class | R | 135-2001 | 1 | 2 | R |  | P
| Notification Class | 86 | Priority | R | 135-2001 | 1 | 2 | W |  | M
| Notification Class | 1 | Ack_Required | R | 135-2001 | 1 | 2 | W |  | M
| Notification Class | 102 | Recipient_List | R | 135-2001 | 1 | 2 | W |  | M
| Notification Class | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Notification Class | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
PR (16) | Program | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Program | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Program | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Program | 92 | Program_State | R | 135-2001 | 1 | 2 | R |  | P
| Program | 90 | Program_Change | W | 135-2001 | 1 | 2 | W |  | M
| Program | 100 | Reason_For_Halt | O1 | 135-2001 | 1 | 2 | R |  | P
| Program | 29 | Description_Of_Halt | O1 | 135-2001 | 1 | 2 | R | = Klartext | P
| Program | 91 | Program_Location | O | 135-2001 | 1 | 2 | O |  | P
| Program | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Program | 48 | Instance_Of | O | 135-2001 | 1 | 2 | O |  | P
| Program | 111 | Status_Flags | R | 135-2001 | 1 | 2 | R |  | P
| Program | 103 | Reliability | O | 135-2001 | 1 | 2 | R |  | P
| Program | 81 | Out_Of_Service | R | 135-2001 | 1 | 2 | R |  | P
| Program | 353 | Event_Detection_Enable | O2,3 | 135-2010 Add af | 1 | 13 | R |  | P
| Program | 17 | Notification_Class | O2,3 | 135-2010 Add af | 1 | 13 | W |  | M
| Program | 35 | Event_Enable | O2,3 | 135-2010 Add af | 1 | 13 | W |  | M
| Program | 36 | Event_State | O2,3 | 135-2010 Add af | 1 | 13 | R |  | P
| Program | 0 | Acked_Transitions | O2,3 | 135-2010 Add af | 1 | 13 | R |  | P
| Program | 72 | Notify_Type | O2,3 | 135-2010 Add af | 1 | 13 | W |  | M
| Program | 130 | Event_Time_Stamps | O2,3 | 135-2010 Add af | 1 | 13 | R |  | P
| Program | 351 | Event_Message_Texts | O3 | 135-2010 Add af | 1 | 13 | R |  | P
| Program | 352 | Event_Message_Texts_Config | O3 | 135-2010 Add af | 1 | 13 | W |  | M
| Program | 357 | Reliability_Evaluation_Inhibit | O4 | 135-2010 Add af | 1 | 13 | W |  | M
| Program | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Program | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
SCHED (17) | Schedule | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Schedule | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Schedule | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Schedule | 85 | Present_Value | R | 135-2001 | 1 | 2 | R |  | P
| Schedule | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Schedule | 32 | Effective_Period | R | 135-2001 | 1 | 2 | W |  | M
| Schedule | 123 | Weekly_Schedule | O1 | 135-2001 | 1 | 2 | W |  | M
| Schedule | 38 | Exception_Schedule | O1 | 135-2001 | 1 | 2 | W |  | M
| Schedule | 174 | Schedule_Default | R | 135-2001 Add a | 1 | 4 | R |  | P
| Schedule | 54 | List_Of_Object_Property_References | R | 135-2001 | 1 | 2 | R |  | P
| Schedule | 88 | Priority_For_Writing | R | 135-2001 | 1 | 2 | R |  | P
| Schedule | 111 | Status_Flags | R | 135-2001 Add a | 1 | 4 | R |  | P
| Schedule | 103 | Reliability | R | 135-2001 Add a | 1 | 4 | R |  | P
| Schedule | 81 | Out_Of_Service | R | 135-2001 Add a | 1 | 4 | R |  | M
| Schedule | 353 | Event_Detection_Enable | O2,3 | 135-2010 Add af | 1 | 13 | R |  | P
| Schedule | 17 | Notification_Class | O2,3 | 135-2010 Add af | 1 | 13 | W |  | M
| Schedule | 35 | Event_Enable | O2,3 | 135-2010 Add af | 1 | 13 | W |  | M
| Schedule | 36 | Event_State | O2,3 | 135-2010 Add af | 1 | 13 | R |  | P
| Schedule | 0 | Acked_Transitions | O2,3 | 135-2010 Add af | 1 | 13 | R |  | P
| Schedule | 72 | Notify_Type | O2,3 | 135-2010 Add af | 1 | 13 | W |  | M
| Schedule | 130 | Event_Time_Stamps | O2,3 | 135-2010 Add af | 1 | 13 | R |  | P
| Schedule | 351 | Event_Message_Texts | O3 | 135-2010 Add af | 1 | 13 | R |  | P
| Schedule | 352 | Event_Message_Texts_Config | O3 | 135-2010 Add af | 1 | 13 | W |  | M
| Schedule | 357 | Reliability_Evaluation_Inhibit | O | 135-2010 Add af | 1 | 13 | W |  | M
| Schedule | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Schedule | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
AVG (18) | Averaging | 75 | Object_Identifier | R | 135-2001 | 1 | 2
| Averaging | 77 | Object_Name | R | 135-2001 | 1 | 2
| Averaging | 79 | Object_Type | R | 135-2001 | 1 | 2
| Averaging | 136 | Minimum_Value | R | 135-2001 | 1 | 2
| Averaging | 150 | Minimum_Value_Timestamp | O | 135-2001 | 1 | 2
| Averaging | 125 | Average_Value | R | 135-2001 | 1 | 2
| Averaging | 151 | Variance_Value | O | 135-2001 | 1 | 2
| Averaging | 135 | Maximum_Value | R | 135-2001 | 1 | 2
| Averaging | 149 | Maximum_Value_Timestamp | O | 135-2001 | 1 | 2
| Averaging | 28 | Description | O | 135-2001 | 1 | 2
| Averaging | 124 | Attempted_Samples | W1 | 135-2001 | 1 | 2
| Averaging | 146 | Valid_Samples | R | 135-2001 | 1 | 2
| Averaging | 78 | Object_Property_Reference | R1 | 135-2001 | 1 | 2
| Averaging | 147 | Window_Interval | W1 | 135-2001 | 1 | 2
| Averaging | 148 | Window_Samples | W1 | 135-2001 | 1 | 2
| Averaging | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Averaging | 168 | Profile_Name | O | 135-2001 | 1 | 2
MV (19) | Multi-state Value | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Value | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Multi-state Value | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Value | 85 | Present_Value | R1 | 135-2001 | 1 | 2 | R1 |  | M
| Multi-state Value | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Multi-state Value | 111 | Status_Flags | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Value | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Value | 103 | Reliability | O2 | 135-2001 | 1 | 2 | R |  | P
| Multi-state Value | 81 | Out_Of_Service | R | 135-2001 | 1 | 2 | W |  | M
| Multi-state Value | 74 | Number_Of_States | R | 135-2001 | 1 | 2 | R |  | P
| Multi-state Value | 110 | State_Text | O | 135-2001 | 1 | 2 | R |  | M
| Multi-state Value | 87 | Priority_Array | O3 | 135-2001 | 1 | 2 | R |  | P
| Multi-state Value | 104 | Relinquish_Default | O3 | 135-2001 | 1 | 2 | W |  | M
| Multi-state Value | 113 | Time_Delay | O4,6 | 135-2001 | 1 | 2 | W |  | M
| Multi-state Value | 17 | Notification_Class | O4,6 | 135-2001 | 1 | 2 | W |  | M
| Multi-state Value | 7 | Alarm_Values | O4,6 | 135-2001 | 1 | 2 | R |  | M
| Multi-state Value | 39 | Fault_Values | O8 | 135-2001 | 1 | 2 | R |  | M
| Multi-state Value | 35 | Event_Enable | O4,6 | 135-2001 | 1 | 2 | W |  | M
| Multi-state Value | 0 | Acked_Transitions | O4,6 | 135-2001 | 1 | 2 | R |  | P
| Multi-state Value | 72 | Notify_Type | O4,6 | 135-2001 | 1 | 2 | R |  | M
| Multi-state Value | 130 | Event_Time_Stamps | O4,6 | 135-2001 | 1 | 2 | R |  | P
| Multi-state Value | 351 | Event_Message_Texts | O5,6 | 135-2008 Add z | 1 | 11 | R |  | P
| Multi-state Value | 352 | Event_Message_Texts_Config | O6 | 135-2010 Add af | 1 | 13 | W |  | M
| Multi-state Value | 353 | Event_Detection_Enable | O4,6 | 135-2010 Add af | 1 | 13 | R |  | P
| Multi-state Value | 355 | Event_Algorithm_Inhibit_Ref | O6 | 135-2010 Add af | 1 | 13 | R |  | P
| Multi-state Value | 354 | Event_Algorithm_Inhibit | O6,7 | 135-2010 Add af | 1 | 13 | W |  | M
| Multi-state Value | 356 | Time_Delay_Normal | O6 | 135-2010 Add af | 1 | 13 | W |  | M
| Multi-state Value | 357 | Reliability_Evaluation_Inhibit | O8 | 135-2010 Add af | 1 | 13 | W |  | M
| Multi-state Value | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Multi-state Value | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
TL (20) | Trend Log | 75 | Object_Identifier | R | 135-2001 | 1 | 2 | R |  | P
| Trend Log | 77 | Object_Name | R | 135-2001 | 1 | 2 | R | = BAS | M
| Trend Log | 79 | Object_Type | R | 135-2001 | 1 | 2 | R |  | P
| Trend Log | 28 | Description | O | 135-2001 | 1 | 2 | R | = Klartext | M
| Trend Log | 133 | Enable | W | 135-2004 Add b | 1 | 7 | W |  | M
| Trend Log | 142 | Start_Time | O1,2 | 135-2001 | 1 | 2 | W |  | M
| Trend Log | 143 | Stop_Time | O1,2 | 135-2001 | 1 | 2 | W |  | M
| Trend Log | 132 | Log_DeviceObjectProperty | O8 | 135-2001 | 1 | 2 | R |  | P
| Trend Log | 134 | Log_Interval | O1,3 | 135-2001 | 1 | 2 | W |  | M
| Trend Log | 128 | COV_Resubscription_Interval | O | 135-2001 | 1 | 2 | W |  | M
| Trend Log | 127 | Client_COV_Increment | O | 135-2001 | 1 | 2 | W |  | M
| Trend Log | 144 | Stop_When_Full | R | 135-2001 | 1 | 2 | W |  | M
| Trend Log | 126 | Buffer_Size | R | 135-2001 | 1 | 2 | R |  | P
| Trend Log | 131 | Log_Buffer | R | 135-2001 | 1 | 2 | R |  | P
| Trend Log | 141 | Record_Count | W | 135-2001 | 1 | 2 | W |  | M
| Trend Log | 145 | Total_Record_Count | R | 135-2001 | 1 | 2 | R |  | P
| Trend Log | 197 | Logging_Type | R | 135-2004 Add b | 1 | 7 | R |  | P
| Trend Log | 193 | Align_Intervals | O5 | 135-2004 Add b | 1 | 7 | W |  | M
| Trend Log | 195 | Interval_Offset | O5 | 135-2004 Add b | 1 | 7 | R |  | P
| Trend Log | 205 | Trigger | O | 135-2004 Add b | 1 | 7 | W |  | M
| Trend Log | 111 | Status_Flags | R | 135-2004 Add b | 1 | 7 | R |  | P
| Trend Log | 103 | Reliability | O | 135-2004 Add b | 1 | 7 | R |  | P
| Trend Log | 137 | Notification_Threshold | O4,7 | 135-2001 | 1 | 2 | W |  | M
| Trend Log | 140 | Records_Since_Notification | O4,7 | 135-2001 | 1 | 2 | R |  | P
| Trend Log | 173 | Last_Notify_Record | O4,7 | 135-2004 Add b | 1 | 7 | R |  | P
| Trend Log | 36 | Event_State | R | 135-2001 | 1 | 2 | R |  | P
| Trend Log | 17 | Notification_Class | O4,7 | 135-2001 | 1 | 2 | W |  | M
| Trend Log | 35 | Event_Enable | O4,7 | 135-2001 | 1 | 2 | W |  | M
| Trend Log | 0 | Acked_Transitions | O4,7 | 135-2001 | 1 | 2 | R |  | P
| Trend Log | 72 | Notify_Type | O4,7 | 135-2001 | 1 | 2 | R |  | M
| Trend Log | 130 | Event_Time_Stamps | O4,7 | 135-2001 | 1 | 2 | R |  | P
| Trend Log | 351 | Event_Message_Texts | O6,7 | 135-2008 Add z | 1 | 11 | R |  | P
| Trend Log | 352 | Event_Message_Texts_Config | O7 | 135-2010 Add af | 1 | 13 | W |  | P
| Trend Log | 353 | Event_Detection_Enable | O4,7 | 135-2010 Add af | 1 | 13 | R |  | P
| Trend Log | 355 | Event_Algorithm_Inhibit_Ref | O7 | 135-2010 Add af | 1 | 13 | R |  | P
| Trend Log | 354 | Event_Algorithm_Inhibit | O7,9 | 135-2010 Add af | 1 | 13 | W |  | M
| Trend Log | 357 | Reliability_Evaluation_Inhibit | O10 | 135-2010 Add af | 1 | 13 | W |  | M
| Trend Log | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Trend Log | 168 | Profile_Name | O | 135-2001 | 1 | 2 | O |  | P
LSP (21) | Life Safety Point | 75 | Object_Identifier | R | 135-2001 | 1 | 2
| Life Safety Point | 77 | Object_Name | R | 135-2001 | 1 | 2
| Life Safety Point | 79 | Object_Type | R | 135-2001 | 1 | 2
| Life Safety Point | 85 | Present_Value | R | 135-2001 Add a | 1 | 4
| Life Safety Point | 164 | Tracking_Value | R1 | 135-2001 Add a | 1 | 4
| Life Safety Point | 28 | Description | O | 135-2001 | 1 | 2
| Life Safety Point | 31 | Device_Type | O | 135-2001 | 1 | 2
| Life Safety Point | 111 | Status_Flags | R | 135-2001 | 1 | 2
| Life Safety Point | 36 | Event_State | R | 135-2001 | 1 | 2
| Life Safety Point | 103 | Reliability | R1 | 135-2001 | 1 | 2
| Life Safety Point | 81 | Out_Of_Service | R | 135-2001 | 1 | 2
| Life Safety Point | 160 | Mode | W | 135-2001 | 1 | 2
| Life Safety Point | 175 | Accepted_Modes | R | 135-2001 Add c | 1 | 4
| Life Safety Point | 113 | Time_Delay | O2,5 | 135-2001 | 1 | 2
| Life Safety Point | 17 | Notification_Class | O2,5 | 135-2001 | 1 | 2
| Life Safety Point | 166 | Life_Safety_Alarm_Values | O2,5 | 135-2001 | 1 | 2
| Life Safety Point | 7 | Alarm_Values | O2,5 | 135-2001 | 1 | 2
| Life Safety Point | 39 | Fault_Values | O | 135-2001 | 1 | 2
| Life Safety Point | 35 | Event_Enable | O2,5 | 135-2001 | 1 | 2
| Life Safety Point | 0 | Acked_Transitions | O2,5 | 135-2001 | 1 | 2
| Life Safety Point | 72 | Notify_Type | O2,5 | 135-2001 | 1 | 2
| Life Safety Point | 130 | Event_Time_Stamps | O2,5 | 135-2001 | 1 | 2
| Life Safety Point | 351 | Event_Message_Texts | O4,5 | 135-2010 Add af | 1 | 13
| Life Safety Point | 352 | Event_Message_Texts_Config | O5 | 135-2010 Add af | 1 | 13
| Life Safety Point | 353 | Event_Detection_Enable | O2,5 | 135-2010 Add af | 1 | 13
| Life Safety Point | 355 | Event_Algorithm_Inhibit_Ref | O5 | 135-2010 Add af | 1 | 13
| Life Safety Point | 354 | Event_Algorithm_Inhibit | O5,6 | 135-2010 Add af | 1 | 13
| Life Safety Point | 356 | Time_Delay_Normal | O5 | 135-2010 Add af | 1 | 13
| Life Safety Point | 357 | Reliability_Evaluation_Inhibit | O | 135-2010 Add af | 1 | 13
| Life Safety Point | 163 | Silenced | R | 135-2001 | 1 | 2
| Life Safety Point | 161 | Operation_Expected | R | 135-2001 | 1 | 2
| Life Safety Point | 158 | Maintenance_Required | O | 135-2001 | 1 | 2
| Life Safety Point | 162 | Setting | O | 135-2001 | 1 | 2
| Life Safety Point | 156 | Direct_Reading | O3 | 135-2001 | 1 | 2
| Life Safety Point | 117 | Units | O3 | 135-2001 | 1 | 2
| Life Safety Point | 159 | Member_Of | O | 135-2001 | 1 | 2
| Life Safety Point | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Life Safety Point | 168 | Profile_Name | O | 135-2001 | 1 | 2
LSZ (22) | Life Safety Zone | 75 | Object_Identifier | R | 135-2001 | 1 | 2
| Life Safety Zone | 77 | Object_Name | R | 135-2001 | 1 | 2
| Life Safety Zone | 79 | Object_Type | R | 135-2001 | 1 | 2
| Life Safety Zone | 85 | Present_Value | R | 135-2001 Add a | 1 | 4
| Life Safety Zone | 164 | Tracking_Value | R1 | 135-2001 Add a | 1 | 4
| Life Safety Zone | 28 | Description | O | 135-2001 | 1 | 2
| Life Safety Zone | 31 | Device_Type | O | 135-2001 | 1 | 2
| Life Safety Zone | 111 | Status_Flags | R | 135-2001 | 1 | 2
| Life Safety Zone | 36 | Event_State | R | 135-2001 | 1 | 2
| Life Safety Zone | 103 | Reliability | R1 | 135-2001 | 1 | 2
| Life Safety Zone | 81 | Out_Of_Service | R | 135-2001 | 1 | 2
| Life Safety Zone | 160 | Mode | W | 135-2001 | 1 | 2
| Life Safety Zone | 175 | Accepted_Modes | R | 135-2001 Add c | 1 | 4
| Life Safety Zone | 113 | Time_Delay | O2,4 | 135-2001 | 1 | 2
| Life Safety Zone | 17 | Notification_Class | O2,4 | 135-2001 | 1 | 2
| Life Safety Zone | 166 | Life_Safety_Alarm_Values | O2,4 | 135-2001 | 1 | 2
| Life Safety Zone | 7 | Alarm_Values | O2,4 | 135-2001 | 1 | 2
| Life Safety Zone | 39 | Fault_Values | O | 135-2001 | 1 | 2
| Life Safety Zone | 35 | Event_Enable | O2,4 | 135-2001 | 1 | 2
| Life Safety Zone | 0 | Acked_Transitions | O2,4 | 135-2001 | 1 | 2
| Life Safety Zone | 72 | Notify_Type | O2,4 | 135-2001 | 1 | 2
| Life Safety Zone | 130 | Event_Time_Stamps | O2,4 | 135-2001 | 1 | 2
| Life Safety Zone | 351 | Event_Message_Texts | O3,4 | 135-2010 Add af | 1 | 13
| Life Safety Zone | 352 | Event_Message_Texts_Config | O4 | 135-2010 Add af | 1 | 13
| Life Safety Zone | 353 | Event_Detection_Enable | O2,4 | 135-2010 Add af | 1 | 13
| Life Safety Zone | 355 | Event_Algorithm_Inhibit_Ref | O4 | 135-2010 Add af | 1 | 13
| Life Safety Zone | 354 | Event_Algorithm_Inhibit | O4,5 | 135-2010 Add af | 1 | 13
| Life Safety Zone | 356 | Time_Delay_Normal | O4 | 135-2010 Add af | 1 | 13
| Life Safety Zone | 357 | Reliability_Evaluation_Inhibit | O | 135-2010 Add af | 1 | 13
| Life Safety Zone | 163 | Silenced | R | 135-2001 | 1 | 2
| Life Safety Zone | 161 | Operation_Expected | R | 135-2001 | 1 | 2
| Life Safety Zone | 158 | Maintenance_Required | O | 135-2001 | 1 | 2
| Life Safety Zone | 165 | Zone_Members | R | 135-2001 | 1 | 2
| Life Safety Zone | 159 | Member_Of | O | 135-2001 | 1 | 2
| Life Safety Zone | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Life Safety Zone | 168 | Profile_Name | O | 135-2001 | 1 | 2
ACC (23) | Accumulator | 75 | Object_Identifier | R | 135-2001 Add c | 1 | 4
| Accumulator | 77 | Object_Name | R | 135-2001 Add c | 1 | 4
| Accumulator | 79 | Object_Type | R | 135-2001 Add c | 1 | 4
| Accumulator | 85 | Present_Value | R1 | 135-2001 Add c | 1 | 4
| Accumulator | 28 | Description | O | 135-2001 Add c | 1 | 4
| Accumulator | 31 | Device_Type | O | 135-2001 Add c | 1 | 4
| Accumulator | 111 | Status_Flags | R | 135-2001 Add c | 1 | 4
| Accumulator | 36 | Event_State | R | 135-2001 Add c | 1 | 4
| Accumulator | 103 | Reliability | O | 135-2001 Add c | 1 | 4
| Accumulator | 81 | Out_Of_Service | R | 135-2001 Add c | 1 | 4
| Accumulator | 187 | Scale | R | 135-2001 Add c | 1 | 4
| Accumulator | 117 | Units | R | 135-2001 Add c | 1 | 4
| Accumulator | 185 | Prescale | O | 135-2001 Add c | 1 | 4
| Accumulator | 65 | Max_Pres_Value | R | 135-2001 Add c | 1 | 4
| Accumulator | 192 | Value_Change_Time | O2 | 135-2001 Add c | 1 | 4
| Accumulator | 190 | Value_Before_Change | O2,3 | 135-2001 Add c | 1 | 4
| Accumulator | 191 | Value_Set | O2,3 | 135-2001 Add c | 1 | 4
| Accumulator | 184 | Logging_Record | O | 135-2001 Add c | 1 | 4
| Accumulator | 183 | Logging_Object | O | 135-2001 Add c | 1 | 4
| Accumulator | 186 | Pulse_Rate | O1,4,7 | 135-2001 Add c | 1 | 4
| Accumulator | 45 | High_Limit | O4,6 | 135-2001 Add c | 1 | 4
| Accumulator | 59 | Low_Limit | O4,6 | 135-2001 Add c | 1 | 4
| Accumulator | 182 | Limit_Monitoring_Interval | O4,7 | 135-2001 Add c | 1 | 4
| Accumulator | 17 | Notification_Class | O4,6 | 135-2001 Add c | 1 | 4
| Accumulator | 113 | Time_Delay | O4,6 | 135-2001 Add c | 1 | 4
| Accumulator | 52 | Limit_Enable | O4,6 | 135-2001 Add c | 1 | 4
| Accumulator | 35 | Event_Enable | O4,6 | 135-2001 Add c | 1 | 4
| Accumulator | 0 | Acked_Transitions | O4,6 | 135-2001 Add c | 1 | 4
| Accumulator | 72 | Notify_Type | O4,6 | 135-2001 Add c | 1 | 4
| Accumulator | 130 | Event_Time_Stamps | O4,6 | 135-2001 Add c | 1 | 4
| Accumulator | 351 | Event_Message_Texts | O5,6 | 135-2008 Add z | 1 | 11
| Accumulator | 352 | Event_Message_Texts_Config | O6 | 135-2010 Add af | 1 | 13
| Accumulator | 353 | Event_Detection_Enable | O4,6 | 135-2010 Add af | 1 | 13
| Accumulator | 355 | Event_Algorithm_Inhibit_Ref | O6 | 135-2010 Add af | 1 | 13
| Accumulator | 354 | Event_Algorithm_Inhibit | O6,8 | 135-2010 Add af | 1 | 13
| Accumulator | 356 | Time_Delay_Normal | O6 | 135-2010 Add af | 1 | 13
| Accumulator | 357 | Reliability_Evaluation_Inhibit | O9 | 135-2010 Add af | 1 | 13
| Accumulator | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Accumulator | 168 | Profile_Name | O | 135-2001 Add c | 1 | 14
PC (24) | Pulse Converter | 75 | Object_Identifier | R | 135-2001 Add c | 1 | 4 | R |  | P
| Pulse Converter | 77 | Object_Name | R | 135-2001 Add c | 1 | 4 | R |  | M
| Pulse Converter | 79 | Object_Type | R | 135-2001 Add c | 1 | 4 | R |  | P
| Pulse Converter | 28 | Description | O | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 85 | Present_Value | R1 | 135-2001 Add c | 1 | 4 | R1 | R1=W wenn Out_Of_Service = WAHR | M
| Pulse Converter | 181 | Input_Reference | O | 135-2001 Add c | 1 | 4 | O |  | P
| Pulse Converter | 111 | Status_Flags | R | 135-2001 Add c | 1 | 4 | R |  | P
| Pulse Converter | 36 | Event_State | R | 135-2001 Add c | 1 | 4 | R |  | P
| Pulse Converter | 103 | Reliability | O | 135-2001 Add c | 1 | 4 | R |  | P
| Pulse Converter | 81 | Out_Of_Service | R | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 117 | Units | R | 135-2001 Add c | 1 | 4 | R |  | P
| Pulse Converter | 188 | Scale_Factor | R | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 176 | Adjust_Value | W | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 177 | Count | R | 135-2001 Add c | 1 | 4 | R |  | P
| Pulse Converter | 189 | Update_Time | R | 135-2001 Add c | 1 | 4 | R |  | P
| Pulse Converter | 179 | Count_Change_Time | R | 135-2001 Add c | 1 | 4 | R2 |  | P
| Pulse Converter | 178 | Count_Before_Change | R | 135-2001 Add c | 1 | 4 | R2 |  | P
| Pulse Converter | 22 | COV_Increment | O2 | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 180 | COV_Period | O2 | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 17 | Notification_Class | O3,5 | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 113 | Time_Delay | O3,5 | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 45 | High_Limit | O3,5 | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 59 | Low_Limit | O3,5 | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 25 | Deadband | O3,5 | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 52 | Limit_Enable | O3,5 | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 35 | Event_Enable | O3,5 | 135-2001 Add c | 1 | 4 | W |  | M
| Pulse Converter | 0 | Acked_Transitions | O3,5 | 135-2001 Add c | 1 | 4 | R |  | P
| Pulse Converter | 72 | Notify_Type | O3,5 | 135-2001 Add c | 1 | 4 | R |  | M
| Pulse Converter | 130 | Event_Time_Stamps | O3,5 | 135-2001 Add c | 1 | 4 | R |  | P
| Pulse Converter | 351 | Event_Message_Texts | O4,5 | 135-2008 Add z | 1 | 11 | R |  | P
| Pulse Converter | 352 | Event_Message_Texts_Config | O5 | 135-2010 Add af | 1 | 13 | W |  | M
| Pulse Converter | 353 | Event_Detection_Enable | O3,5 | 135-2010 Add af | 1 | 13 | R |  | P
| Pulse Converter | 355 | Event_Algorithm_Inhibit_Ref | O5 | 135-2010 Add af | 1 | 13 | R |  | P
| Pulse Converter | 354 | Event_Algorithm_Inhibit | O5,6 | 135-2010 Add af | 1 | 13 | W |  | M
| Pulse Converter | 356 | Time_Delay_Normal | O5 | 135-2010 Add af | 1 | 13 | W |  | M
| Pulse Converter | 357 | Reliability_Evaluation_Inhibit | O7 | 135-2010 Add af | 1 | 13 | W |  | M
| Pulse Converter | 371 | Property_List | R | 135-2010 Add ao | 1 | 14 | R |  | P
| Pulse Converter | 168 | Profile_Name | O | 135-2001 Add c | 1 | 4 | O |  | P
EL (25) | Event Log | 75 | Object_Identifier | R | 135-2004 Add b | 1 | 7
| Event Log | 77 | Object_Name | R | 135-2004 Add b | 1 | 7
| Event Log | 79 | Object_Type | R | 135-2004 Add b | 1 | 7
| Event Log | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Event Log | 28 | Description | O | 135-2004 Add b | 1 | 7
| Event Log | 111 | Status_Flags | R | 135-2004 Add b | 1 | 7
| Event Log | 36 | Event_State | R | 135-2004 Add b | 1 | 7
| Event Log | 103 | Reliability | O | 135-2004 Add b | 1 | 7
| Event Log | 133 | Enable | W | 135-2004 Add b | 1 | 7
| Event Log | 142 | Start_Time | O1,2 | 135-2004 Add b | 1 | 7
| Event Log | 143 | Stop_Time | O1,2 | 135-2004 Add b | 1 | 7
| Event Log | 144 | Stop_When_Full | R | 135-2004 Add b | 1 | 7
| Event Log | 126 | Buffer_Size | R | 135-2004 Add b | 1 | 7
| Event Log | 131 | Log_Buffer | R | 135-2004 Add b | 1 | 7
| Event Log | 141 | Record_Count | W | 135-2004 Add b | 1 | 7
| Event Log | 145 | Total_Record_Count | R | 135-2004 Add b | 1 | 7
| Event Log | 137 | Notification_Threshold | O3,5 | 135-2004 Add b | 1 | 7
| Event Log | 140 | Records_Since_Notification | O3,5 | 135-2004 Add b | 1 | 7
| Event Log | 173 | Last_Notify_Record | O3,5 | 135-2004 Add b | 1 | 7
| Event Log | 17 | Notification_Class | O3,5 | 135-2004 Add b | 1 | 7
| Event Log | 35 | Event_Enable | O3,5 | 135-2004 Add b | 1 | 7
| Event Log | 0 | Acked_Transitions | O3,5 | 135-2004 Add b | 1 | 7
| Event Log | 72 | Notify_Type | O3,5 | 135-2004 Add b | 1 | 7
| Event Log | 130 | Event_Time_Stamps | O3,5 | 135-2004 Add b | 1 | 7
| Event Log | 351 | Event_Message_Texts | O4,5 | 135-2008 Add z | 1 | 11
| Event Log | 352 | Event_Message_Texts_Config | O5 | 135-2010 Add af | 1 | 13
| Event Log | 353 | Event_Detection_Enable | O3,5 | 135-2010 Add af | 1 | 13
| Event Log | 355 | Event_Algorithm_Inhibit_Ref | O5 | 135-2010 Add af | 1 | 13
| Event Log | 354 | Event_Algorithm_Inhibit | O5,6 | 135-2010 Add af | 1 | 13
| Event Log | 357 | Reliability_Evaluation_Inhibit | O7 | 135-2010 Add af | 1 | 13
| Event Log | 168 | Profile_Name | O | 135-2004 Add b | 1 | 7
GGRP (26) | Global Group | 75 | Object_Identifier | R | 135-2008 Add p | 1 | 11
| Global Group | 77 | Object_Name | R | 135-2008 Add p | 1 | 11
| Global Group | 79 | Object_Type | R | 135-2008 Add p | 1 | 11
| Global Group | 28 | Description | O | 135-2008 Add p | 1 | 11
| Global Group | 345 | Group_Members | R | 135-2008 Add p | 1 | 11
| Global Group | 346 | Group_Member_Names | O | 135-2008 Add p | 1 | 11
| Global Group | 85 | Present_Value | R | 135-2008 Add p | 1 | 11
| Global Group | 111 | Status_Flags | R | 135-2008 Add p | 1 | 11
| Global Group | 36 | Event_State | R | 135-2008 Add p | 1 | 11
| Global Group | 347 | Member_Status_Flags | R | 135-2008 Add p | 1 | 11
| Global Group | 103 | Reliability | O | 135-2008 Add p | 1 | 11
| Global Group | 81 | Out_of_Service | R | 135-2008 Add p | 1 | 11
| Global Group | 118 | Update_Interval | O | 135-2008 Add p | 1 | 11
| Global Group | 348 | Requested_Update_Interval | O | 135-2008 Add p | 1 | 11
| Global Group | 128 | COV_Resubscription_Interval | O | 135-2008 Add p | 1 | 11
| Global Group | 127 | Client_COV_Increment | O | 135-2008 Add p | 1 | 11
| Global Group | 113 | Time_Delay | O1,4 | 135-2008 Add p | 1 | 11
| Global Group | 17 | Notification_Class | O1,4 | 135-2008 Add p | 1 | 11
| Global Group | 35 | Event_Enable | O1,4 | 135-2008 Add p | 1 | 11
| Global Group | 0 | Acked_Transitions | O1,4 | 135-2008 Add p | 1 | 11
| Global Group | 72 | Notify_Type | O1,4 | 135-2008 Add p | 1 | 11
| Global Group | 130 | Event_Time_Stamps | O1,4 | 135-2008 Add p | 1 | 11
| Global Group | 351 | Event_Message_Texts | O3,4 | 135-2010 Add af | 1 | 13
| Global Group | 352 | Event_Message_Texts_Config | O4 | 135-2010 Add af | 1 | 13
| Global Group | 353 | Event_Detection_Enable | O1,4 | 135-2010 Add af | 1 | 13
| Global Group | 355 | Event_Algorithm_Inhibit_Ref | O4 | 135-2010 Add af | 1 | 13
| Global Group | 354 | Event_Algorithm_Inhibit | O4,5 | 135-2010 Add af | 1 | 13
| Global Group | 356 | Time_Delay_Normal | O4 | 135-2010 Add af | 1 | 13
| Global Group | 349 | COVU_Period | O2 | 135-2008 Add p | 1 | 11
| Global Group | 350 | COVU_Recipients | O2 | 135-2008 Add p | 1 | 11
| Global Group | 357 | Reliability_Evaluation_Inhibit | O6 | 135-2010 Add af | 1 | 13
| Global Group | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Global Group | 168 | Profile_Name | O | 135-2004 Add b | 1 | 7
TLOGM (27) | Trend Log Multiple | 75 | Object_Identifier | R | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 77 | Object_Name | R | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 79 | Object_Type | R | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 28 | Description | O | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 111 | Status_Flags | R | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 36 | Event_State | R | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 103 | Reliability | O | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 133 | Enable | W | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 142 | Start_Time | O1 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 143 | Stop_Time | O1 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 132 | Log_DeviceObjectProperty | R | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 197 | Logging_Type | R | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 134 | Log_Interval | R2 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 193 | Align_Intervals | O3 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 195 | Interval_Offset | O3 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 205 | Trigger | O | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 144 | Stop_When_Full | R | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 126 | Buffer_Size | R | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 131 | Log_Buffer | R | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 141 | Record_Count | W | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 145 | Total_Record_Count | R | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 137 | Notification_Threshold | O4,6 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 140 | Records_Since_Notification | O4,6 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 173 | Last_Notify_Record | O4,6 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 17 | Notification_Class | O4,6 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 35 | Event_Enable | O4,6 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 0 | Acked_Transitions | O4,6 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 72 | Notify_Type | O4,6 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 130 | Event_Time_Stamps | O4,6 | 135-2004 Add b | 1 | 7
| Trend Log Multiple | 351 | Event_Message_Texts | O5,6 | 135-2008 Add z | 1 | 11
| Trend Log Multiple | 352 | Event_Message_Texts_Config | O6 | 135-2010 Add af | 1 | 13
| Trend Log Multiple | 353 | Event_Detection_Enable | O4,6 | 135-2010 Add af | 1 | 13
| Trend Log Multiple | 355 | Event_Algorithm_Inhibit_Ref | O6 | 135-2010 Add af | 1 | 13
| Trend Log Multiple | 354 | Event_Algorithm_Inhibit | O6,7 | 135-2010 Add af | 1 | 13
| Trend Log Multiple | 357 | Reliability_Evaluation_Inhibit | O8 | 135-2010 Add af | 1 | 13
| Trend Log Multiple | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Trend Log Multiple | 168 | Profile_Name | O | 135-2004 Add b | 1 | 7
LOC (28) | Load Control | 75 | Object_Identifier | R | 135-2004 Add e | 1 | 6
| Load Control | 77 | Object_Name | R | 135-2004 Add e | 1 | 6
| Load Control | 79 | Object_Type | R | 135-2004 Add e | 1 | 6
| Load Control | 28 | Description | O | 135-2004 Add e | 1 | 6
| Load Control | 85 | Present_Value | R | 135-2004 Add e | 1 | 6
| Load Control | 222 | State_Description | O | 135-2004 Add e | 1 | 6
| Load Control | 111 | Status_Flags | R | 135-2004 Add e | 1 | 6
| Load Control | 36 | Event_State | R | 135-2004 Add e | 1 | 6
| Load Control | 103 | Reliability | O | 135-2004 Add e | 1 | 6
| Load Control | 218 | Requested_Shed_Level | W | 135-2004 Add e | 1 | 6
| Load Control | 142 | Start_Time | W | 135-2004 Add e | 1 | 6
| Load Control | 219 | Shed_Duration | W | 135-2004 Add e | 1 | 6
| Load Control | 213 | Duty_Window | W | 135-2004 Add e | 1 | 6
| Load Control | 133 | Enable | W | 135-2004 Add e | 1 | 6
| Load Control | 215 | Full_Duty_Baseline | O | 135-2004 Add e | 1 | 6
| Load Control | 214 | Expected_Shed_Level | R | 135-2004 Add e | 1 | 6
| Load Control | 212 | Actual_Shed_Level | R | 135-2004 Add e | 1 | 6
| Load Control | 221 | Shed_Levels | W1 | 135-2004 Add e | 1 | 6
| Load Control | 220 | Shed_Level_Descriptions | R | 135-2004 Add e | 1 | 6
| Load Control | 17 | Notification_Class | O2,4 | 135-2004 Add e | 1 | 6
| Load Control | 113 | Time_Delay | O2,4 | 135-2004 Add e | 1 | 6
| Load Control | 35 | Event_Enable | O2,4 | 135-2004 Add e | 1 | 6
| Load Control | 0 | Acked_Transitions | O2,4 | 135-2004 Add e | 1 | 6
| Load Control | 72 | Notify_Type | O2,4 | 135-2004 Add e | 1 | 6
| Load Control | 130 | Event_Time_Stamps | O2,4 | 135-2004 Add e | 1 | 6
| Load Control | 351 | Event_Message_Texts | O3,4 | 135-2008 Add z | 1 | 11
| Load Control | 352 | Event_Message_Texts_Config | O4 | 135-2010 Add af | 1 | 13
| Load Control | 353 | Event_Detection_Enable | O2,4 | 135-2010 Add af | 1 | 13
| Load Control | 355 | Event_Algorithm_Inhibit_Ref | O4 | 135-2010 Add af | 1 | 13
| Load Control | 354 | Event_Algorithm_Inhibit | O4,5 | 135-2010 Add af | 1 | 13
| Load Control | 356 | Time_Delay_Normal | O4 | 135-2010 Add af | 1 | 13
| Load Control | 357 | Reliability_Evaluation_Inhibit | O6 | 135-2010 Add af | 1 | 13
| Load Control | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Load Control | 168 | Profile_Name | O | 135-2004 Add e | 1 | 6
SV (29) | Structured View | 75 | Object_Identifier | R | 135-2004 Add d | 1 | 5
| Structured View | 77 | Object_Name | R | 135-2004 Add d | 1 | 5
| Structured View | 79 | Object_Type | R | 135-2004 Add d | 1 | 5
| Structured View | 28 | Description | O | 135-2004 Add d | 1 | 5
| Structured View | 208 | Node_Type | R | 135-2004 Add d | 1 | 5
| Structured View | 207 | Node_Subtype | O | 135-2004 Add d | 1 | 5
| Structured View | 211 | Subordinate_List | R | 135-2004 Add d | 1 | 5
| Structured View | 210 | Subordinate_Annotations | O | 135-2004 Add d | 1 | 5
| Structured View | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Structured View | 168 | Profile_Name | O | 135-2004 Add d | 1 | 5
ACD (30) | Access Door | 75 | Object_Identifier | R | 135-2001 Add f | 1 | 6
| Access Door | 77 | Object_Name | R | 135-2004 Add f | 1 | 6
| Access Door | 79 | Object_Type | R | 135-2004 Add f | 1 | 6
| Access Door | 85 | Present_Value | W | 135-2004 Add f | 1 | 6
| Access Door | 28 | Description | O | 135-2004 Add f | 1 | 6
| Access Door | 111 | Status_Flags | R | 135-2004 Add f | 1 | 6
| Access Door | 36 | Event_State | R | 135-2004 Add f | 1 | 6
| Access Door | 103 | Reliability | R | 135-2004 Add f | 1 | 6
| Access Door | 81 | Out_Of_Service | R | 135-2004 Add f | 1 | 6
| Access Door | 87 | Priority_Array | R | 135-2004 Add f | 1 | 6
| Access Door | 104 | Relinquish_Default | R | 135-2004 Add f | 1 | 6
| Access Door | 231 | Door_Status | O1,2 | 135-2004 Add f | 1 | 6
| Access Door | 233 | Lock_Status | O1 | 135-2004 Add f | 1 | 6
| Access Door | 235 | Secured_Status | O | 135-2004 Add f | 1 | 6
| Access Door | 228 | Door_Members | O | 135-2004 Add f | 1 | 6
| Access Door | 230 | Door_Pulse_Time | R | 135-2004 Add f | 1 | 6
| Access Door | 227 | Door_Extended_Pulse_Time | R | 135-2004 Add f | 1 | 6
| Access Door | 232 | Door_Unlock_Delay_Time | O | 135-2004 Add f | 1 | 6
| Access Door | 229 | Door_Open_Too_Long_Time | R | 135-2004 Add f | 1 | 6
| Access Door | 226 | Door_Alarm_State | O3 | 135-2004 Add f | 1 | 6
| Access Door | 234 | Masked_Alarm_Values | O | 135-2004 Add f | 1 | 6
| Access Door | 158 | Maintenance_Required | O | 135-2004 Add f | 1 | 6
| Access Door | 113 | Time_Delay | O3,5 | 135-2004 Add f | 1 | 6
| Access Door | 17 | Notification_Class | O3,5 | 135-2004 Add f | 1 | 6
| Access Door | 7 | Alarm_Values | O3,5 | 135-2004 Add f | 1 | 6
| Access Door | 39 | Fault_Values | O | 135-2004 Add f | 1 | 6
| Access Door | 35 | Event_Enable | O3,5 | 135-2004 Add f | 1 | 6
| Access Door | 0 | Acked_Transitions | O3,5 | 135-2004 Add f | 1 | 6
| Access Door | 72 | Notify_Type | O3,5 | 135-2004 Add f | 1 | 6
| Access Door | 130 | Event_Time_Stamps | O3,5 | 135-2004 Add f | 1 | 6
| Access Door | 351 | Event_Message_Texts | O4,5 | 135-2008 Add z | 1 | 11
| Access Door | 352 | Event_Message_Texts_Config | O5 | 135-2010 Add af | 1 | 13
| Access Door | 353 | Event_Detection_Enable | O3,5 | 135-2010 Add af | 1 | 13
| Access Door | 355 | Event_Algorithm_Inhibit_Ref | O5 | 135-2010 Add af | 1 | 13
| Access Door | 354 | Event_Algorithm_Inhibit | O5,6 | 135-2010 Add af | 1 | 13
| Access Door | 356 | Time_Delay_Normal | O5 | 135-2010 Add af | 1 | 13
| Access Door | 357 | Reliability_Evaluation_Inhibit | O | 135-2010 Add af | 1 | 13
| Access Door | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Access Door | 168 | Profile_Name | O | 135-2004 Add f | 1 | 6
TIM (31) | Timer | 75 | Object_Identifier | R | 135-2012 Add ay | 1 | 17
| Timer | 77 | Object_Name | R | 135-2012 Add ay | 1 | 17
| Timer | 79 | Object_Type | R | 135-2012 Add ay | 1 | 17
| Timer | 28 | Description | O | 135-2012 Add ay | 1 | 17
| Timer | 85 | Present_Value | R1 | 135-2012 Add ay | 1 | 17
| Timer | 111 | Status_Flags | R | 135-2012 Add ay | 1 | 17
| Timer | 36 | Event_State | O3 | 135-2012 Add ay | 1 | 17
| Timer | 103 | Reliability | O1 | 135-2012 Add ay | 1 | 17
| Timer | 81 | Out_Of_Service | O | 135-2012 Add ay | 1 | 17
| Timer | 398 | Timer_State | R2 | 135-2012 Add ay | 1 | 17
| Timer | 397 | Timer_Running | R2 | 135-2012 Add ay | 1 | 17
| Timer | 189 | Update_Time | O3 | 135-2012 Add ay | 1 | 17
| Timer | 395 | Last_State_Change | O | 135-2012 Add ay | 1 | 17
| Timer | 270 | Expiration_Time | O | 135-2012 Add ay | 1 | 17
| Timer | 394 | Initial_Timeout | O | 135-2012 Add ay | 1 | 17
| Timer | 393 | Default_Timeout | O | 135-2012 Add ay | 1 | 17
| Timer | 69 | Min_Pres_Value | O4 | 135-2012 Add ay | 1 | 17
| Timer | 65 | Max_Pres_Value | O4 | 135-2012 Add ay | 1 | 17
| Timer | 106 | Resolution | O | 135-2012 Add ay | 1 | 17
| Timer | 396 | State_Change_Values | O5 | 135-2012 Add ay | 1 | 17
| Timer | 54 | List_Of_Object_Property_References | O5 | 135-2012 Add ay | 1 | 17
| Timer | 88 | Priority_For_Writing | O5 | 135-2012 Add ay | 1 | 17
| Timer | 353 | Event_Detection_Enable | O3,6 | 135-2012 Add ay | 1 | 17
| Timer | 17 | Notification_Class | O3,6 | 135-2012 Add ay | 1 | 17
| Timer | 113 | Time_Delay | O3,6 | 135-2012 Add ay | 1 | 17
| Timer | 356 | Time_Delay_Normal | O3,6 | 135-2012 Add ay | 1 | 17
| Timer | 7 | Alarm_Values | O3,6 | 135-2012 Add ay | 1 | 17
| Timer | 35 | Event_Enable | O3,6 | 135-2012 Add ay | 1 | 17
| Timer | 1 | Acked_Transitions | O3,6 | 135-2012 Add ay | 1 | 17
| Timer | 72 | Notify_Type | O3,6 | 135-2012 Add ay | 1 | 17
| Timer | 130 | Event_Time_Stamps | O3,6 | 135-2012 Add ay | 1 | 17
| Timer | 351 | Event_Message_Texts | O6 | 135-2012 Add ay | 1 | 17
| Timer | 352 | Event_Message_Texts_Config | O6 | 135-2012 Add ay | 1 | 17
| Timer | 355 | Event_Algorithm_Inhibit_Ref | O6 | 135-2012 Add ay | 1 | 17
| Timer | 354 | Event_Algorithm_Inhibit | O6,7 | 135-2012 Add ay | 1 | 17
| Timer | 357 | Reliability_Evaluation_Inhibit | O8 | 135-2012 Add ay | 1 | 17
| Timer | 371 | Property_List | R | 135-2012 Add ay | 1 | 17
| Timer | 168 | Profile_Name | O | 135-2012 Add ay | 1 | 17
AC (32) | Access Credential | 75 | Object_Identifier | R | 135-2008 Add j | 1 | 9
| Access Credential | 77 | Object_Name | R | 135-2008 Add j | 1 | 9
| Access Credential | 79 | Object_Type | R | 135-2008 Add j | 1 | 9
| Access Credential | 28 | Description | O | 135-2008 Add j | 1 | 9
| Access Credential | 323 | Global_Identifier | W | 135-2008 Add j | 1 | 9
| Access Credential | 111 | Status_Flags | R | 135-2008 Add j | 1 | 9
| Access Credential | 103 | Reliability | R | 135-2008 Add j | 1 | 9
| Access Credential | 264 | Credential_Status | R | 135-2008 Add j | 1 | 9
| Access Credential | 303 | Reason_For_Disable | R | 135-2008 Add j | 1 | 9
| Access Credential | 257 | Authentication_Factors | R | 135-2008 Add j | 1 | 9
| Access Credential | 254 | Activation_Time | R | 135-2008 Add j | 1 | 9
| Access Credential | 270 | Expiry_Time | R | 135-2008 Add j | 1 | 9
| Access Credential | 263 | Credential_Disable | R | 135-2008 Add j | 1 | 9
| Access Credential | 267 | Days_Remaining | O1 | 135-2008 Add j | 1 | 9
| Access Credential | 319 | Uses_Remaining | O | 135-2008 Add j | 1 | 9
| Access Credential | 244 | Absentee_Limit | O1 | 135-2008 Add j | 1 | 9
| Access Credential | 262 | Belongs_To | O | 135-2008 Add j | 1 | 9
| Access Credential | 256 | Assigned_Access_Rights | R | 135-2008 Add j | 1 | 9
| Access Credential | 276 | Last_Access_Point | O | 135-2008 Add j | 1 | 9
| Access Credential | 275 | Last_Access_Event | O | 135-2008 Add j | 1 | 9
| Access Credential | 281 | Last_Use_Time | O | 135-2008 Add j | 1 | 9
| Access Credential | 308 | Trace_Flag | O | 135-2008 Add j | 1 | 9
| Access Credential | 306 | Threat_Authority | O | 135-2008 Add j | 1 | 9
| Access Credential | 271 | Extended_Time_Enable | O | 135-2008 Add j | 1 | 9
| Access Credential | 364 | Authorization_Exemptions | O | 135-2010 Add ae | 1 | 13
| Access Credential | 357 | Reliability_Evaluation_Inhibit | O | 135-2010 Add ae | 1 | 13
| Access Credential | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Access Credential | 168 | Profile_Name | O | 135-2008 Add j | 1 | 9
ACP (33) | Access Point | 75 | Object_Identifier | R | 135-2008 Add j | 1 | 9
| Access Point | 77 | Object_Name | R | 135-2008 Add j | 1 | 9
| Access Point | 79 | Object_Type | R | 135-2008 Add j | 1 | 9
| Access Point | 28 | Description | O | 135-2008 Add j | 1 | 9
| Access Point | 111 | Status_Flags | R | 135-2008 Add j | 1 | 9
| Access Point | 36 | Event_State | R | 135-2008 Add j | 1 | 9
| Access Point | 103 | Reliability | R | 135-2008 Add j | 1 | 9
| Access Point | 81 | Out_Of_Service | R | 135-2008 Add j | 1 | 9
| Access Point | 260 | Authentication_Status | R | 135-2008 Add j | 1 | 9
| Access Point | 255 | Active_Authentication_Policy | R | 135-2008 Add j | 1 | 9
| Access Point | 289 | Number_Of_Authentication_Policies | R | 135-2008 Add j | 1 | 9
| Access Point | 258 | Authentication_Policy_List | O1 | 135-2008 Add j | 1 | 9
| Access Point | 259 | Authentication_Policy_Names | O1 | 135-2008 Add j | 1 | 9
| Access Point | 261 | Authorization_Mode | R | 135-2008 Add j | 1 | 9
| Access Point | 326 | Verification_Time | O | 135-2008 Add j | 1 | 9
| Access Point | 282 | Lockout | O2 | 135-2008 Add j | 1 | 9
| Access Point | 283 | Lockout_Relinquish_Time | O | 135-2008 Add j | 1 | 9
| Access Point | 273 | Failed_Attempts | O | 135-2008 Add j | 1 | 9
| Access Point | 272 | Failed_Attempt_Events | O | 135-2008 Add j | 1 | 9
| Access Point | 285 | Max_Failed_Attempts | O3 | 135-2008 Add j | 1 | 9
| Access Point | 274 | Failed_Attempts_Time | O3 | 135-2008 Add j | 1 | 9
| Access Point | 307 | Threat_Level | O | 135-2008 Add j | 1 | 9
| Access Point | 298 | Occupancy_Upper_Limit_Enforced | O | 135-2008 Add j | 1 | 9
| Access Point | 295 | Occupancy_Lower_Limit_Enforced | O | 135-2008 Add j | 1 | 9
| Access Point | 291 | Occupancy_Count_Adjust | O | 135-2008 Add j | 1 | 9
| Access Point | 253 | Accompaniment_Time | O | 135-2008 Add j | 1 | 9
| Access Point | 247 | Access_Event | R | 135-2008 Add j | 1 | 9
| Access Point | 322 | Access_Event_Tag | R | 135-2008 Add j | 1 | 9
| Access Point | 250 | Access_Event_Time | R | 135-2008 Add j | 1 | 9
| Access Point | 249 | Access_Event_Credential | R | 135-2008 Add j | 1 | 9
| Access Point | 248 | Access_Event_Authentication_Factor | O | 135-2008 Add j | 1 | 9
| Access Point | 246 | Access_Doors | R | 135-2008 Add j | 1 | 9
| Access Point | 88 | Priority_For_Writing | R | 135-2008 Add j | 1 | 9
| Access Point | 287 | Muster_Point | O | 135-2008 Add j | 1 | 9
| Access Point | 321 | Zone_To | O | 135-2008 Add j | 1 | 9
| Access Point | 320 | Zone_From | O | 135-2008 Add j | 1 | 9
| Access Point | 17 | Notification_Class | O4,6 | 135-2008 Add j | 1 | 9
| Access Point | 309 | Transaction_Notification_Class | O | 135-2008 Add j | 1 | 9
| Access Point | 245 | Access_Alarm_Events | O4,6 | 135-2008 Add j | 1 | 9
| Access Point | 251 | Access_Transaction_Events | O4,6 | 135-2008 Add j | 1 | 9
| Access Point | 35 | Event_Enable | O4,6 | 135-2008 Add j | 1 | 9
| Access Point | 0 | Acked_Transitions | O4,6 | 135-2008 Add j | 1 | 9
| Access Point | 72 | Notify_Type | O4,6 | 135-2008 Add j | 1 | 9
| Access Point | 130 | Event_Time_Stamps | O4,6 | 135-2008 Add j | 1 | 9
| Access Point | 351 | Event_Message_Texts | O5,6 | 135-2008 Add z | 1 | 11
| Access Point | 352 | Event_Message_Texts_Config | O6 | 135-2010 Add af | 1 | 13
| Access Point | 353 | Event_Detection_Enable | O4,6 | 135-2010 Add af | 1 | 13
| Access Point | 355 | Event_Algorithm_Inhibit_Ref | O6 | 135-2010 Add af | 1 | 13
| Access Point | 354 | Event_Algorithm_Inhibit | O6,7 | 135-2010 Add af | 1 | 13
| Access Point | 357 | Reliability_Evaluation_Inhibit | O | 135-2010 Add af | 1 | 13
| Access Point | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Access Point | 168 | Profile_Name | O | 135-2008 Add j | 1 | 9
ACR (34) | Access Rights | 75 | Object_Identifier | R | 135-2008 Add j | 1 | 9
| Access Rights | 77 | Object_Name | R | 135-2008 Add j | 1 | 9
| Access Rights | 79 | Object_Type | R | 135-2008 Add j | 1 | 9
| Access Rights | 28 | Description | O | 135-2008 Add j | 1 | 9
| Access Rights | 323 | Global_Identifier | W | 135-2008 Add j | 1 | 9
| Access Rights | 111 | Status_Flags | R | 135-2008 Add j | 1 | 9
| Access Rights | 103 | Reliability | R | 135-2008 Add j | 1 | 9
| Access Rights | 133 | Enable | R | 135-2008 Add j | 1 | 9
| Access Rights | 288 | Negative_Access_Rules | R | 135-2008 Add j | 1 | 9
| Access Rights | 302 | Positive_Access_Rules | R | 135-2008 Add j | 1 | 9
| Access Rights | 252 | Accompaniment | O | 135-2008 Add j | 1 | 9
| Access Rights | 357 | Reliability_Evaluation_Inhibit | O | 135-2010 Add af | 1 | 13
| Access Rights | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Access Rights | 168 | Profile_Name | O | 135-2008 Add j | 1 | 9
ACU (35) | Access User | 75 | Object_Identifier | R | 135-2008 Add j | 1 | 9
| Access User | 77 | Object_Name | R | 135-2008 Add j | 1 | 9
| Access User | 79 | Object_Type | R | 135-2008 Add j | 1 | 9
| Access User | 28 | Description | O | 135-2008 Add j | 1 | 9
| Access User | 323 | Global_Identifier | W | 135-2008 Add j | 1 | 9
| Access User | 111 | Status_Flags | R | 135-2008 Add j | 1 | 9
| Access User | 103 | Reliability | R | 135-2008 Add j | 1 | 9
| Access User | 318 | User_Type | R | 135-2008 Add j | 1 | 9
| Access User | 317 | User_Name | O | 135-2008 Add j | 1 | 9
| Access User | 310 | User_External_Identifier | O | 135-2008 Add j | 1 | 9
| Access User | 311 | User_Information_Reference | O | 135-2008 Add j | 1 | 9
| Access User | 286 | Members | O | 135-2008 Add j | 1 | 9
| Access User | 159 | Member_Of | O | 135-2008 Add j | 1 | 9
| Access User | 265 | Credentials | R | 135-2008 Add j | 1 | 9
| Access User | 357 | Reliability_Evaluation_Inhibit | O | 135-2010 Add af | 1 | 13
| Access User | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Access User | 168 | Profile_Name | O | 135-2008 Add j | 1 | 9
ACZ (36) | Access Zone | 75 | Object_Identifier | R | 135-2008 Add j | 1 | 9
| Access Zone | 77 | Object_Name | R | 135-2008 Add j | 1 | 9
| Access Zone | 79 | Object_Type | R | 135-2008 Add j | 1 | 9
| Access Zone | 28 | Description | O | 135-2008 Add j | 1 | 9
| Access Zone | 323 | Global_Identifier | W | 135-2008 Add j | 1 | 9
| Access Zone | 296 | Occupancy_State | R | 135-2008 Add j | 1 | 9
| Access Zone | 111 | Status_Flags | R | 135-2008 Add j | 1 | 9
| Access Zone | 36 | Event_State | R | 135-2008 Add j | 1 | 9
| Access Zone | 103 | Reliability | R1 | 135-2008 Add j | 1 | 9
| Access Zone | 81 | Out_Of_Service | R | 135-2008 Add j | 1 | 9
| Access Zone | 290 | Occupancy_Count | O1,3,4 | 135-2008 Add j | 1 | 9
| Access Zone | 292 | Occupancy_Count_Enable | O3,4 | 135-2008 Add j | 1 | 9
| Access Zone | 176 | Adjust_Value | O3,4,5 | 135-2008 Add j | 1 | 9
| Access Zone | 297 | Occupancy_Upper_Limit | O | 135-2008 Add j | 1 | 9
| Access Zone | 294 | Occupancy_Lower_Limit | O | 135-2008 Add j | 1 | 9
| Access Zone | 266 | Credentials_In_Zone | O | 135-2008 Add j | 1 | 9
| Access Zone | 277 | Last_Credential_Added | O | 135-2008 Add j | 1 | 9
| Access Zone | 278 | Last_Credential_Added_Time | O | 135-2008 Add j | 1 | 9
| Access Zone | 279 | Last_Credential_Removed | O | 135-2008 Add j | 1 | 9
| Access Zone | 280 | Last_Credential_Removed_Time | O | 135-2008 Add j | 1 | 9
| Access Zone | 300 | Passback_Mode | O | 135-2008 Add j | 1 | 9
| Access Zone | 301 | Passback_Timeout | O2 | 135-2008 Add j | 1 | 9
| Access Zone | 268 | Entry_Points | R | 135-2008 Add j | 1 | 9
| Access Zone | 269 | Exit_Points | R | 135-2008 Add j | 1 | 9
| Access Zone | 113 | Time_Delay | O3,7 | 135-2008 Add j | 1 | 9
| Access Zone | 17 | Notification_Class | O3,7 | 135-2008 Add j | 1 | 9
| Access Zone | 7 | Alarm_Values | O3,7 | 135-2008 Add j | 1 | 9
| Access Zone | 35 | Event_Enable | O3,7 | 135-2008 Add j | 1 | 9
| Access Zone | 0 | Acked_Transitions | O3,7 | 135-2008 Add j | 1 | 9
| Access Zone | 72 | Notify_Type | O3,7 | 135-2008 Add j | 1 | 9
| Access Zone | 130 | Event_Time_Stamps | O3,7 | 135-2008 Add j | 1 | 9
| Access Zone | 351 | Event_Message_Texts | O6,7 | 135-2008 Add z | 1 | 11
| Access Zone | 352 | Event_Message_Texts_Config | O7 | 135-2010 Add af | 1 | 13
| Access Zone | 353 | Event_Detection_Enable | O3,7 | 135-2010 Add af | 1 | 13
| Access Zone | 355 | Event_Algorithm_Inhibit_Ref | O7 | 135-2010 Add af | 1 | 13
| Access Zone | 354 | Event_Algorithm_Inhibit | O7,8 | 135-2010 Add af | 1 | 13
| Access Zone | 356 | Time_Delay_Normal | O7 | 135-2010 Add af | 1 | 13
| Access Zone | 357 | Reliability_Evaluation_Inhibit | O | 135-2010 Add af | 1 | 13
| Access Zone | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Access Zone | 168 | Profile_Name | O | 135-2008 Add j | 1 | 9
CDI (37) | Credential Data Input | 75 | Object_Identifier | R | 135-2008 Add j | 1 | 9
| Credential Data Input | 77 | Object_Name | R | 135-2008 Add j | 1 | 9
| Credential Data Input | 79 | Object_Type | R | 135-2008 Add j | 1 | 9
| Credential Data Input | 85 | Present_Value | R1 | 135-2008 Add j | 1 | 9
| Credential Data Input | 28 | Description | O | 135-2008 Add j | 1 | 9
| Credential Data Input | 111 | Status_Flags | R | 135-2008 Add j | 1 | 9
| Credential Data Input | 103 | Reliability | R1 | 135-2008 Add j | 1 | 9
| Credential Data Input | 81 | Out_Of_Service | R | 135-2008 Add j | 1 | 9
| Credential Data Input | 304 | Supported_Formats | R | 135-2008 Add j | 1 | 9
| Credential Data Input | 305 | Supported_Format_Classes | O2 | 135-2008 Add j | 1 | 9
| Credential Data Input | 189 | Update_Time | R | 135-2008 Add j | 1 | 9
| Credential Data Input | 353 | Event_Detection_Enable | O3,4 | 135-2010 Add af | 1 | 13
| Credential Data Input | 17 | Notification_Class | O3,4 | 135-2010 Add af | 1 | 13
| Credential Data Input | 35 | Event_Enable | O3,4 | 135-2010 Add af | 1 | 13
| Credential Data Input | 36 | Event_State | O3,4 | 135-2010 Add af | 1 | 13
| Credential Data Input | 0 | Acked_Transitions | O3,4 | 135-2010 Add af | 1 | 13
| Credential Data Input | 72 | Notify_Type | O3,4 | 135-2010 Add af | 1 | 13
| Credential Data Input | 130 | Event_Time_Stamps | O3,4 | 135-2010 Add af | 1 | 13
| Credential Data Input | 351 | Event_Message_Texts | O4 | 135-2010 Add af | 1 | 13
| Credential Data Input | 352 | Event_Message_Texts_Config | O4 | 135-2010 Add af | 1 | 13
| Credential Data Input | 357 | Reliability_Evaluation_Inhibit | O | 135-2010 Add af | 1 | 13
| Credential Data Input | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Credential Data Input | 168 | Profile_Name | O | 135-2008 Add j | 1 | 9
NS (38) | Network Security | 75 | Object_Identifier | R | 135-2008 Add g | 1 | 11
| Network Security | 77 | Object_Name | R | 135-2008 Add g | 1 | 11
| Network Security | 79 | Object_Type | R | 135-2008 Add g | 1 | 11
| Network Security | 28 | Description | O | 135-2008 Add g | 1 | 11
| Network Security | 327 | Base_Device_Security_Policy | W | 135-2008 Add g | 1 | 11
| Network Security | 332 | Network_Access_Security_Policies | W | 135-2008 Add g | 1 | 11
| Network Security | 335 | Security_Time_Window | W | 135-2008 Add g | 1 | 11
| Network Security | 333 | Packet_Reorder_Time | W | 135-2008 Add g | 1 | 11
| Network Security | 328 | Distribution_Key_Revision | R | 135-2008 Add g | 1 | 11
| Network Security | 330 | Key_Sets | R | 135-2008 Add g | 1 | 11
| Network Security | 331 | Last_Key_Server | W | 135-2008 Add g | 1 | 11
| Network Security | 334 | Security_PDU_Timeout | W | 135-2008 Add g | 1 | 11
| Network Security | 337 | Update_Key_Set_Timeout | R | 135-2008 Add g | 1 | 11
| Network Security | 336 | Supported_Security_Algorithms | R | 135-2008 Add g | 1 | 11
| Network Security | 329 | Do_Not_Hide | W | 135-2008 Add g | 1 | 11
| Network Security | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Network Security | 168 | Profile_Name | O | 135-2004 Add g | 1 | 11
BSV (39) | BitString Value | 75 | Object_Identifier | R
| BitString Value | 77 | Object_Name | R
| BitString Value | 79 | Object_Type | R
| BitString Value | 28 | Description | O
| BitString Value | 85 | Present_Value | R1
| BitString Value | 343 | Bit_Text | O
| BitString Value | 111 | Status_Flags | R
| BitString Value | 36 | Event_State | O3
| BitString Value | 103 | Reliability | O
| BitString Value | 81 | Out_Of_Service | O
| BitString Value | 87 | Priority_Array | O2
| BitString Value | 104 | Relinquish_Default | O2
| BitString Value | 113 | Time_Delay | O3,5
| BitString Value | 17 | Notification_Class | O3,5
| BitString Value | 7 | Alarm_Values | O3,5
| BitString Value | 342 | Bit_Mask | O3,5
| BitString Value | 35 | Event_Enable | O3,5
| BitString Value | 1 | Acked_Transitions | O3,5
| BitString Value | 72 | Notify_Type | O3,5
| BitString Value | 130 | Event_Time_Stamps | O3,5
| BitString Value | 351 | Event_Message_Texts | O4,5
| BitString Value | 352 | Event_Message_Texts_Config | O5
| BitString Value | 353 | Event_Detection_Enable | O3,5
| BitString Value | 355 | Event_Algorithm_Inhibit_Ref | O5
| BitString Value | 354 | Event_Algorithm_Inhibit | O5,6
| BitString Value | 356 | Time_Delay_Normal | O5
| BitString Value | 357 | Reliability_Evaluation_Inhibit | O7
| BitString Value | 371 | Property_List | R
| BitString Value | 168 | Profile_Name | O
CSV (40) | CharacterString Value | 75 | Object_Identifier | R
| CharacterString Value | 77 | Object_Name | R
| CharacterString Value | 79 | Object_Type | R
| CharacterString Value | 28 | Description | O
| CharacterString Value | 85 | Present_Value | R1
| CharacterString Value | 111 | Status_Flags | R
| CharacterString Value | 36 | Event_State | O3
| CharacterString Value | 103 | Reliability | O
| CharacterString Value | 81 | Out_Of_Service | O
| CharacterString Value | 87 | Priority_Array | O2
| CharacterString Value | 104 | Relinquish_Default | O2
| CharacterString Value | 113 | Time_Delay | O3,5
| CharacterString Value | 17 | Notification_Class | O3,5
| CharacterString Value | 7 | Alarm_Values | O3,5
| CharacterString Value | 39 | Fault_Values | O7
| CharacterString Value | 35 | Event_Enable | O3,5
| CharacterString Value | 1 | Acked_Transitions | O3,5
| CharacterString Value | 72 | Notify_Type | O3,5
| CharacterString Value | 130 | Event_Time_Stamps | O3,5
| CharacterString Value | 351 | Event_Message_Texts | O4,5
| CharacterString Value | 352 | Event_Message_Texts_Config | O5
| CharacterString Value | 353 | Event_Detection_Enable | O3,5
| CharacterString Value | 355 | Event_Algorithm_Inhibit_Ref | O5
| CharacterString Value | 354 | Event_Algorithm_Inhibit | O5,6
| CharacterString Value | 356 | Time_Delay_Normal | O5
| CharacterString Value | 357 | Reliability_Evaluation_Inhibit | O7
| CharacterString Value | 371 | Property_List | R
| CharacterString Value | 168 | Profile_Name | O
DPV (41) | Date Pattern Value | 75 | Object_Identifier | R
| Date Pattern Value | 77 | Object_Name | R
| Date Pattern Value | 79 | Object_Type | R
| Date Pattern Value | 28 | Description | O
| Date Pattern Value | 85 | Present_Value | R1
| Date Pattern Value | 111 | Status_Flags | R
| Date Pattern Value | 36 | Event_State | O
| Date Pattern Value | 103 | Reliability | O
| Date Pattern Value | 81 | Out_Of_Service | O
| Date Pattern Value | 87 | Priority_Array | O2
| Date Pattern Value | 104 | Relinquish_Default | O2
| Date Pattern Value | 357 | Reliability_Evaluation_Inhibit | O3
| Date Pattern Value | 371 | Property_List | R
| Date Pattern Value | 168 | Profile_Name | O
DV (42) | Date Value | 75 | Object_Identifier | R
| Date Value | 77 | Object_Name | R
| Date Value | 79 | Object_Type | R
| Date Value | 28 | Description | O
| Date Value | 85 | Present_Value | R1
| Date Value | 111 | Status_Flags | R
| Date Value | 36 | Event_State | O
| Date Value | 103 | Reliability | O
| Date Value | 81 | Out_Of_Service | O
| Date Value | 87 | Priority_Array | O2
| Date Value | 104 | Relinquish_Default | O2
| Date Value | 357 | Reliability_Evaluation_Inhibit | O3
| Date Value | 371 | Property_List | R
| Date Value | 168 | Profile_Name | O
DTPV (43) | DateTime-Pattern-Value | 75 | Object_Identifier | R
| DateTime-Pattern-Value | 77 | Object_Name | R
| DateTime-Pattern-Value | 79 | Object_Type | R
| DateTime-Pattern-Value | 28 | Description | O
| DateTime-Pattern-Value | 85 | Present_Value | R1
| DateTime-Pattern-Value | 111 | Status_Flags | R
| DateTime-Pattern-Value | 36 | Event_State | O
| DateTime-Pattern-Value | 103 | Reliability | O
| DateTime-Pattern-Value | 81 | Out_Of_Service | O
| DateTime-Pattern-Value | 344 | Is_UTC | O
| DateTime-Pattern-Value | 87 | Priority_Array | O2
| DateTime-Pattern-Value | 104 | Relinquish_Default | O2
| DateTime-Pattern-Value | 357 | Reliability_Evaluation_Inhibit | O3
| DateTime-Pattern-Value | 371 | Property_List | R
| DateTime-Pattern-Value | 168 | Profile_Name | O
DTV (44) | DateTime Value | 75 | Object_Identifier | R
| DateTime-Value | 77 | Object_Name | R
| DateTime-Value | 79 | Object_Type | R
| DateTime-Value | 28 | Description | O
| DateTime-Value | 85 | Present_Value | R1
| DateTime-Value | 111 | Status_Flags | R
| DateTime-Value | 36 | Event_State | O
| DateTime-Value | 103 | Reliability | O
| DateTime-Value | 81 | Out_Of_Service | O
| DateTime-Value | 87 | Priority_Array | O2
| DateTime-Value | 104 | Relinquish_Default | O2
| DateTime-Value | 344 | Is_UTC | O
| DateTime-Value | 357 | Reliability_Evaluation_Inhibit | O3
| DateTime-Value | 371 | Property_List | R
| DateTime-Value | 168 | Profile_Name | O
IV (45) | Integer Value | 75 | Object_Identifier | R
| Integer Value | 77 | Object_Name | R
| Integer Value | 79 | Object_Type | R
| Integer Value | 28 | Description | O
| Integer Value | 85 | Present_Value | R1
| Integer Value | 111 | Status_Flags | R
| Integer Value | 36 | Event_State | O4
| Integer Value | 103 | Reliability | O
| Integer Value | 81 | Out_Of_Service | O
| Integer Value | 117 | Units | R
| Integer Value | 87 | Priority_Array | O2
| Integer Value | 104 | Relinquish_Default | O2
| Integer Value | 22 | COV_Increment | O3
| Integer Value | 113 | Time_Delay | O4,6
| Integer Value | 17 | Notification_Class | O4,6
| Integer Value | 45 | High_Limit | O4,6
| Integer Value | 59 | Low_Limit | O4,6
| Integer Value | 25 | Deadband | O4,6
| Integer Value | 52 | Limit_Enable | O4,6
| Integer Value | 35 | Event_Enable | O4,6
| Integer Value | 1 | Acked_Transitions | O4,6
| Integer Value | 72 | Notify_Type | O4,6
| Integer Value | 130 | Event_Time_Stamps | O4,6
| Integer Value | 351 | Event_Message_Texts | O5,6
| Integer Value | 352 | Event_Message_Texts_Config | O6
| Integer Value | 353 | Event_Detection_Enable | O4,6
| Integer Value | 355 | Event_Algorithm_Inhibit_Ref | O6
| Integer Value | 354 | Event_Algorithm_Inhibit | O6,7
| Integer Value | 356 | Time_Delay_Normal | O6
| Integer Value | 357 | Reliability_Evaluation_Inhibit | O8
| Integer Value | 69 | Min_Pres_Value | O
| Integer Value | 65 | Max_Pres_Value | O
| Integer Value | 106 | Resolution | O
| Integer Value | 371 | Property_List | R
| Integer Value | 168 | Profile_Name | O
LAV (46) | Large Analog Value | 75 | Object_Identifier | R
| Large Analog Value | 77 | Object_Name | R
| Large Analog Value | 79 | Object_Type | R
| Large Analog Value | 28 | Description | O
| Large Analog Value | 85 | Present_Value | R1
| Large Analog Value | 111 | Status_Flags | R
| Large Analog Value | 36 | Event_State | O4
| Large Analog Value | 103 | Reliability | O
| Large Analog Value | 81 | Out_Of_Service | O
| Large Analog Value | 117 | Units | R
| Large Analog Value | 87 | Priority_Array | O2
| Large Analog Value | 104 | Relinquish_Default | O2
| Large Analog Value | 22 | COV_Increment | O3
| Large Analog Value | 113 | Time_Delay | O4,6
| Large Analog Value | 17 | Notification_Class | O4,6
| Large Analog Value | 45 | High_Limit | O4,6
| Large Analog Value | 59 | Low_Limit | O4,6
| Large Analog Value | 25 | Deadband | O4,6
| Large Analog Value | 52 | Limit_Enable | O4,6
| Large Analog Value | 35 | Event_Enable | O4,6
| Large Analog Value | 1 | Acked_Transitions | O4,6
| Large Analog Value | 72 | Notify_Type | O4,6
| Large Analog Value | 130 | Event_Time_Stamps | O4,6
| Large Analog Value | 351 | Event_Message_Texts | O5,6
| Large Analog Value | 352 | Event_Message_Texts_Config | O6
| Large Analog Value | 353 | Event_Detection_Enable | O4,6
| Large Analog Value | 355 | Event_Algorithm_Inhibit_Ref | O6
| Large Analog Value | 354 | Event_Algorithm_Inhibit | O6,7
| Large Analog Value | 356 | Time_Delay_Normal | O6
| Large Analog Value | 357 | Reliability_Evaluation_Inhibit | O8
| Large Analog Value | 69 | Min_Pres_Value | O
| Large Analog Value | 65 | Max_Pres_Value | O
| Large Analog Value | 106 | Resolution | O
| Large Analog Value | 371 | Property_List | R
| Large Analog Value | 168 | Profile_Name | O
OSV (47) | Octetstring Value | 75 | Object_Identifier | R
| Octetstring Value | 77 | Object_Name | R
| Octetstring Value | 79 | Object_Type | R
| Octetstring Value | 28 | Description | O
| Octetstring Value | 85 | Present_Value | R1
| Octetstring Value | 111 | Status_Flags | R
| Octetstring Value | 36 | Event_State | O
| Octetstring Value | 103 | Reliability | O
| Octetstring Value | 81 | Out_Of_Service | O
| Octetstring Value | 87 | Priority_Array | O2
| Octetstring Value | 104 | Relinquish_Default | O2
| Octetstring Value | 357 | Reliability_Evaluation_Inhibit | O3
| Octetstring Value | 371 | Property_List | R
| Octetstring Value | 168 | Profile_Name | O
PIV (48) | Positive Integer Value | 75 | Object_Identifier | R
| Positive Integer Value | 77 | Object_Name | R
| Positive Integer Value | 79 | Object_Type | R
| Positive Integer Value | 28 | Description | O
| Positive Integer Value | 85 | Present_Value | R1
| Positive Integer Value | 111 | Status_Flags | R
| Positive Integer Value | 36 | Event_State | O4
| Positive Integer Value | 103 | Reliability | O
| Positive Integer Value | 81 | Out_Of_Service | O
| Positive Integer Value | 117 | Units | R
| Positive Integer Value | 87 | Priority_Array | O2
| Positive Integer Value | 104 | Relinquish_Default | O2
| Positive Integer Value | 22 | COV_Increment | O3
| Positive Integer Value | 113 | Time_Delay | O4,6
| Positive Integer Value | 17 | Notification_Class | O4,6
| Positive Integer Value | 45 | High_Limit | O4,6
| Positive Integer Value | 59 | Low_Limit | O4,6
| Positive Integer Value | 25 | Deadband | O4,6
| Positive Integer Value | 52 | Limit_Enable | O4,6
| Positive Integer Value | 35 | Event_Enable | O4,6
| Positive Integer Value | 1 | Acked_Transitions | O4,6
| Positive Integer Value | 72 | Notify_Type | O4,6
| Positive Integer Value | 130 | Event_Time_Stamps | O4,6
| Positive Integer Value | 351 | Event_Message_Texts | O5,6
| Positive Integer Value | 352 | Event_Message_Texts_Config | O6
| Positive Integer Value | 353 | Event_Detection_Enable | O4,6
| Positive Integer Value | 355 | Event_Algorithm_Inhibit_Ref | O6
| Positive Integer Value | 354 | Event_Algorithm_Inhibit | O6,7
| Positive Integer Value | 356 | Time_Delay_Normal | O6
| Positive Integer Value | 357 | Reliability_Evaluation_Inhibit | O8
| Positive Integer Value | 69 | Min_Pres_Value | O
| Positive Integer Value | 65 | Max_Pres_Value | O
| Positive Integer Value | 106 | Resolution | O
| Positive Integer Value | 371 | Property_List | R
| Positive Integer Value | 168 | Profile_Name | O
TPV (49) | Time Pattern Value | 75 | Object_Identifier | R
| Time Pattern Value | 77 | Object_Name | R
| Time Pattern Value | 79 | Object_Type | R
| Time Pattern Value | 28 | Description | O
| Time Pattern Value | 85 | Present_Value | R1
| Time Pattern Value | 111 | Status_Flags | R
| Time Pattern Value | 36 | Event_State | O
| Time Pattern Value | 103 | Reliability | O
| Time Pattern Value | 81 | Out_Of_Service | O
| Time Pattern Value | 87 | Priority_Array | O2
| Time Pattern Value | 104 | Relinquish_Default | O2
| Time Pattern Value | 357 | Reliability_Evaluation_Inhibit | O3
| Time Pattern Value | 371 | Property_List | R
| Time Pattern Value | 168 | Profile_Name | O
TV (50) | Time Value | 75 | Object_Identifier | R
| Time Value | 77 | Object_Name | R
| Time Value | 79 | Object_Type | R
| Time Value | 28 | Description | O
| Time Value | 85 | Present_Value | R1
| Time Value | 111 | Status_Flags | R
| Time Value | 36 | Event_State | O
| Time Value | 103 | Reliability | O
| Time Value | 81 | Out_Of_Service | O
| Time Value | 87 | Priority_Array | O2
| Time Value | 104 | Relinquish_Default | O2
| Time Value | 357 | Reliability_Evaluation_Inhibit | O3
| Time Value | 371 | Property_List | R
| Time Value | 168 | Profile_Name | O
NF (51) | Notification Forwarder | 75 | Object_Identifier | R
| Notification Forwarder | 77 | Object_Name | R
| Notification Forwarder | 79 | Object_Type | R
| Notification Forwarder | 28 | Description | O
| Notification Forwarder | 111 | Status_Flags | R
| Notification Forwarder | 103 | Reliability | R
| Notification Forwarder | 81 | Out_Of_Service | R
| Notification Forwarder | 102 | Recipient_List | R
| Notification Forwarder | 362 | Subscribed_Recipients | W
| Notification Forwarder | 361 | Process_Identifier_Filter | R
| Notification Forwarder | 363 | Port_Filter | O1
| Notification Forwarder | 360 | Local_Forwarding_Only | R
| Notification Forwarder | 357 | Reliability_Evaluation_Inhibit | O
| Notification Forwarder | 371 | Property_List | R
| Notification Forwarder | 168 | Profile_Name | O
AE (52) | Alert Enrollment | 75 | Object_Identifier | R
| Alert Enrollment | 77 | Object_Name | R
| Alert Enrollment | 79 | Object_Type | R
| Alert Enrollment | 28 | Description | O
| Alert Enrollment | 85 | Present_Value | R
| Alert Enrollment | 36 | Event_State | R
| Alert Enrollment | 353 | Event_Detection_Enable | R
| Alert Enrollment | 17 | Notification_Class | R
| Alert Enrollment | 35 | Event_Enable | R
| Alert Enrollment | 1 | Acked_Transitions | R
| Alert Enrollment | 72 | Notify_Type | R
| Alert Enrollment | 130 | Event_Time_Stamps | R
| Alert Enrollment | 351 | Event_Message_Texts | O
| Alert Enrollment | 352 | Event_Message_Texts_Config | O
| Alert Enrollment | 355 | Event_Algorithm_Inhibit_Ref | O
| Alert Enrollment | 354 | Event_Algorithm_Inhibit | O
| Alert Enrollment | 371 | Property_List | R
| Alert Enrollment | 168 | Profile_Name | O
CHN (53) | Channel | 75 | Object_Identifier | R
| Channel | 77 | Object_Name | R
| Channel | 79 | Object_Type | R
| Channel | 28 | Description | O
| Channel | 85 | Present_Value | W
| Channel | 369 | Last_Priority | R
| Channel | 370 | Write_Status | R
| Channel | 111 | Status_Flags | R
| Channel | 103 | Reliability | O
| Channel | 81 | Out_Of_Service | R
| Channel | 54 | List_Of_Object_Property_References | W1
| Channel | 368 | Execution_Delay | O1
| Channel | 365 | Allow_Group_Delay_Inhibit | O
| Channel | 366 | Channel_Number | W
| Channel | 367 | Control_Groups | W
| Channel | 353 | Event_Detection_Enable | O2,3
| Channel | 17 | Notification_Class | O2,3
| Channel | 35 | Event_Enable | O2,3
| Channel | 36 | Event_State | O2,3
| Channel | 1 | Acked_Transitions | O2,3
| Channel | 72 | Notify_Type | O2,3
| Channel | 130 | Event_Time_Stamps | O2,3
| Channel | 351 | Event_Message_Texts | O3
| Channel | 352 | Event_Message_Texts_Config | O3
| Channel | 357 | Reliability_Evaluation_Inhibit | O4
| Channel | 371 | Property_List | R
| Channel | 168 | Profile_Name | O
LO (54) | Lighting Output | 75 | Object_Identifier | R | 135-2010 Add i | 1 | 14
| Lighting Output | 77 | Object_Name | R | 135-2010 Add i | 1 | 14
| Lighting Output | 79 | Object_Type | R | 135-2010 Add i | 1 | 14
| Lighting Output | 85 | Present_Value | W | 135-2010 Add i | 1 | 14
| Lighting Output | 164 | Tracking_Value | R | 135-2010 Add i | 1 | 14
| Lighting Output | 380 | Lighting_Command | W | 135-2010 Add i | 1 | 14
| Lighting Output | 378 | In_Progress | R | 135-2010 Add i | 1 | 14
| Lighting Output | 28 | Description | O | 135-2010 Add i | 1 | 14
| Lighting Output | 111 | Status_Flags | R | 135-2010 Add i | 1 | 14
| Lighting Output | 103 | Reliability | O | 135-2010 Add i | 1 | 14
| Lighting Output | 81 | Out_Of_Service | R | 135-2010 Add i | 1 | 14
| Lighting Output | 373 | Blink_Warn_Enable | R | 135-2010 Add i | 1 | 14
| Lighting Output | 377 | Egress_Time | R | 135-2010 Add i | 1 | 14
| Lighting Output | 386 | Egress_Active | R | 135-2010 Add i | 1 | 14
| Lighting Output | 374 | Default_Fade_Time | R | 135-2010 Add i | 1 | 14
| Lighting Output | 375 | Default_Ramp_Rate | R | 135-2010 Add i | 1 | 14
| Lighting Output | 376 | Default_Step_Increment | R | 135-2010 Add i | 1 | 14
| Lighting Output | 385 | Transition | O | 135-2010 Add i | 1 | 14
| Lighting Output | 40 | Feedback_Value | O | 135-2010 Add i | 1 | 14
| Lighting Output | 87 | Priority_Array | R | 135-2010 Add i | 1 | 14
| Lighting Output | 104 | Relinquish_Default | R | 135-2010 Add i | 1 | 14
| Lighting Output | 384 | Power | O | 135-2010 Add i | 1 | 14
| Lighting Output | 379 | Instantaneous_Power | O | 135-2010 Add i | 1 | 14
| Lighting Output | 383 | Min_Actual_Value | O1 | 135-2010 Add i | 1 | 14
| Lighting Output | 382 | Max_Actual_Value | O1 | 135-2010 Add i | 1 | 14
| Lighting Output | 381 | Lighting_Command_Default_Priority | R | 135-2010 Add i | 1 | 14
| Lighting Output | 22 | COV_Increment | O2 | 135-2010 Add i | 1 | 14
| Lighting Output | 357 | Reliability_Evaluation_Inhibit | O3 | 135-2010 Add i | 1 | 14
| Lighting Output | 371 | Property_List | R | 135-2010 Add ao | 1 | 14
| Lighting Output | 168 | Profile_Name | O | 135-2010 Add i | 1 | 14
Dynamische Erzeugung und Löschung von Objekten
CAL | Calendar | [6 empty] | DC / DD |  | DC / DD
EE | Event Enrollment | [6 empty] | DC / DD |  | DC / DD
NC | Notification Class | [6 empty] | DC / DD |  | DC / DD
SCHED | Schedule | [6 empty] | DC / DD |  | DC / DD
TL | Trend Log | [6 empty] | DC / DD |  | DC / DD
EL | Event Log | [6 empty] | DC / DD |  | DC / DD
TLM | Trend Log Multiple | [6 empty] | DC / DD |  | DC / DD
Legende:
Objekte
Anforderungen des AG
Keine Anforderung des AG, bzw. in den behandelten Device-Profilen nicht geforderte Objekte/Properties.
Zukünftige Anforderungen des AG
R | Anpassungen der Anforderungen durch GA Ingenieurgesellschaft mbH
Properties
R | Property muss vorhanden und lesbar sein
W | Property muss vorhanden, lesbar und beschreibbar sein
P | Property muss darstellbar sein
M | Property muss darstellbar und modifizierbar sein
O | Property ist optional
Note on D42: Richard Kwas: zusätzliche Texte, die bei Ereignissübergängen (to offnormal, to fault, to normal) mit übertragen werden
Note on D43: Richard Kwas: Dieses Property enthält Zeichenketten, die Defaultwerte für o.g. "Message Text" der TO-OFFNORMAL, TO_NORMAL, TO-FAULT Ereignismeldung abbilden. Optionall können proprietäre Ersatzkodierungen angewendet werden um eine dynamische Information (z.B. Datum, Zeit) in dem Text einzuschliessen
Note on D44: Richard Kwas: Dieses Property, vom Typ BOOLEAN, zeigt an ab das intrinsic Reporting im Objekt aktiviert wurde und ob das Objekt in ereignisermittelnden Diensten berücksichtigt wird. Dieses Property soll während der Systemkonfiguration eingestellt werden und ist nicht für dynamische Änderungen vorgesehen. Weis dieses Property den Wert FALSE auf, so nimmt das Property Event_State den Wert NORMAL an und die Properties Acked_Transitions, Event_Time_Stamps, Event_Message_Texts nehmen die entsprechenden Werte an. Das Property informiert über die Ereignisunterdrückung im Objekt. Nur wenn der Wert= TRUE ist, dann kann das Objekt sein Zustand (Event_State) ändern und entsprechend den Einstellungen Meldungen generieren.
Note on D45: Richard Kwas: Dieses Property enthält Referenzadresse des Property, das den Wert vom Property Event_Algorithm_Inhibit beeinflusst. Ist der Wert= 4194303 dann durch eine direkte Beschreibung des Property Event_Algorithm_Inhibit können die Zustandsänderungen des Objektes unterdrückt bzw. freigegeben werden. Enthält das Property eine gültige Referenz (Objekt,Property) so wird der Wert aus dem referenzierten Property in das Property Event_Algorithm_Inhibit gemapped.
Note on D46: Richard Kwas: Dieses Property vom Typ BOOLEAN zeigt an ob ein Ereignisalgorithmus (gemäß Kapitel 13.2.2.1, ASHRAE 135-2012) aktiviert/deaktiviertwurde. Dieses Property ist für dynamische anpassungen vorgesehen. Das Property ist nur lesbar, wenn das Referenzproperty i (Event_Algorithm_Inhibit_Ref) ist vorhanden und initilaisiert. Der Wert des Property wiederspiegelt den Wert aus dem Referenzproperty. Werte vom Datentyp BACnetBinaryPV werden in primitiven Datentyp gemapped, ACTIVE->TRUE, INACTIVE-> FALSE. Das Property ist beschreibbar wenn Event_Detection_Enable= TRUE und das Property Event_Algorithm_Inhibit_Ref nicht vorhanden ist bzw. vorhanden aber nicht initialisiert ist. Ist die Referenzierung fehlerhaft so bekommt das Property den Wert FALSE Wenn Event_Detection_Enable= TRUE: Event_Algorithm_Inhibit aktiviert bzw. deaktiviert dynamisch die Ermittlung des Event_State (Übergang zum High-, Low-Limit, Fault)
Note on D48: Richard Kwas: Dieses Property vom Typ BOOLEAN zeigt an ob die Ermittlung der Wertezuverlässigkeit aktiviert/deaktiviert wurde. Dieses Property ist für dynamischen Einsatz vorgesehen. Ist die Ermittlung der Wertezuverlässigkeit deaktiviert so weist das Property Realibilty immer den Wert NO_FAULT_DETECTED an, es sei denn dieser Wert wurde bei Out_Of_Service=TRUE mit anderem Wert überschrieben. Mit dem Property können die Fault Zustände, unabhängig von z. B. High-, Low-Limit unterdrückt werden.
Note on D79: Richard Kwas: Dieses Property enthält Zeichenketten, die ein Basis für den Parameter "Message Text" der TO-OFFNORMAL, TO_NORMAL, TO-FAULT Ereignismeldung darstellen. Optionall können proprietäre Ersatzkodierungen angewendet werden um eine dynamische Information (z.B. Datum, Zeit) in dem Text einzuschliessen
Note on D80: Richard Kwas: Dieses Property, vom Typ BOOLEAN, zeigt an ab das intrinsic Reporting im Objekt aktiviert wurde und ob das Objekt in ereignisermittelnden Diensten berücksichtigt wird. Dieses Property soll während der Systemkonfiguration eingestellt werden und ist nicht für dynamische Änderungen vorgesehen. Weis dieses Property den Wert FALSE auf, so nimmt das Property Event_State den Wert NORMAL an und die Properties Acked_Transitions, Event_Time_Stamps, Event_Message_Texts nehmen die entsprechenden Werte an. Das Property informiert über den Ereignisunterdrückung im Objekt. Nur wenn der Wert= TRUE sit, dann kann das Objekt sein Zustand (Event_State) ändern und entsprechend den Einstellungen Meldungen generieren.
Note on D81: Richard Kwas: Dieses Property enthält Referenzadresse des Property, das den Wert vom Property Event_Algorithm_Inhibit beeinflusst. Ist der Wert= 4194303 dann durch eine direkte Beschreibung des Property Event_Algorithm_Inhibit können die Zustandsänderungen des Objektes unterdrückt bzw. freigegeben werden. Enthält das Property eine gültige Referenz (Objekt,Property) so wird der Wert aus dem referenzierten Property in das Property Event_Algorithm_Inhibit gemapped.
Note on D82: Richard Kwas: Dieses Property vom Typ BOOLEAN zeigt an ob ein Ereignisalgorithmus (gemäß Kapitel 13.2.2.1, ASHRAE 135-2012) aktiviert/deaktiviertwurde. Dieses Property ist für dynamische anpassungen vorgesehen. Das Property ist nur lesbar, wenn das Referenzproperty i (Event_Algorithm_Inhibit_Ref) ist vorhanden und initilaisiert. Der Wert des Property wiederspiegelt den Wert aus dem Referenzproperty. Werte vom Datentyp BACnetBinaryPV werden in primitiven Datentyp gemapped, ACTIVE->TRUE, INACTIVE-> FALSE. Das Property ist beschreibbar wenn Event_Detection_Enable= TRUE und das Property Event_Algorithm_Inhibit_Ref ist nicht vorhanden bzw. vorhanden aber nicht initialisiert. Ist die Referenzierung fehlerhaft so bekommt das Property den Wert FALSE Wenn Event_Detection_Enable= TRUE: Event_Algorithm_Inhibit aktiviert bzw. deaktiviert dynamisch die Ermittlung des Event_State (Übergang zum High-, Low-Limit, Fault)
Note on D84: Richard Kwas: Dieses Property vom Typ BOOLEAN zeigt an ob ein Ermittlung der Wertezuverlässigkeit aktiviert/deaktiviert wurde. Dieses Property ist für dynamischen Einsatz vorgesehen. Ist die Ermittlung der Wertezuverlässigkeit deaktiviert so weist das Property Realibilty immer den Wert NO_FAULT_DETECTED an, es sei denn dieser Wert wurde bei Out_Of_Service=TRUE mit anderem Wert überschrieben. Mit dem Property können die Fault Zustände, unabhängig von z. B. High-, Low-Limit unterdrückt werden.
Note on D327: Richard Kwas: Dieses nur lesbares Property, vom typ BACnetFaultType zeigt an, dass ein FAULT Algorithmus in dem Objekt angewendet wird. none (0), fault-characterstring (1), fault-extended (2), fault-life-safety (3), fault-state (4), fault-status-flags (5)
Note on D328: Richard Kwas: Dieses Property, vom Typ BACnetFaultParameter definiert den, für die Überwachung des referenzierten Objektes angewendeten Fault Algorithmus sowie die, die von dem Algorithmus benötigten Parameter. Das Mapping der Perameter des Fault Algorithmus sind in der Tabelle 12-15.3 dargestellt (ASHRAE 135-2012) Wenn im Event Enrollment Objekt kein Fault Algorithmus angewendet wird, so soll die Fault-Parameter Auswahl (Inhalt des Property Fault_Parameters) den Wert NONE aufweisen.
Note on D329: Richard Kwas: Dieses Property vom Typ BOOLEAN zeigt an ob ein Ermittlung der Wertezuverlässigkeit aktiviert/deaktiviert wurde. Dieses Property ist für dynamischen Einsatz vorgesehen. Ist die Ermittlung der Wertezuverlässigkeit deaktiviert so weist das Property Realibilty immer den Wert NO_FAULT_DETECTED an, es sei denn dieser Wert wurde bei Out_Of_Service=TRUE mit anderem Wert überschrieben. Mit dem Property können die Fault Zustände, unabhängig von z. B. High-, Low-Limit unterdrückt werden.