## BIBBs Selbstauskunft
BACnet INTEROPERABILITY BUILDING BLOCKS gemäß DIN EN ISO 16484-5, Ausgabe:2012-11: Systeme der Gebäudeautomation - Datenkommunikationsprotokoll und ANSI/ASHRAE-Standard 135-2012 | [7 empty] | MBE | AS
BACnet Protocol Version/Revision berücksichtigt: |  |  |  |  | BACnet Protocol |  |  | Universität Bonn | Universität Bonn
BACnet Protocol Version: 1 |  |  |  |  | Version/Revision angewandt: |  |  | UNI_BN2016 | UNI_BN2016
BACnet Protocol Revision: 17
BACnet INTEROPERABILITY BUILDING BLOCKS |  |  |  |  | Protokoll Informationen |  |  | 2016-08-08 | 2016-08-08
|  |  | Initiate (user/client) | Execute (provider/ server) | Quelle ASHRAE | Protocol Version | Protocol Revision | Universität Bonn | Universität Bonn
Kürzel | Bezeichnung | BACnet Dienste |  |  |  | 1 | 14 | MBE | AS
PICS bzw. Testdatum:
Vendor Name:
Product Name:
Product Modell Number:
Applications Software Version:
Firmware Revision:
Protocol Revision:
Data Sharing BIBBs (Objektzugriff, Datenaustauch, gemeinsame Datennutzung)
DS-RP-A | ReadProperty-A | ReadProperty | X |  | 135-2001 | 1 | 2 | J | J
DS-RP-B | ReadProperty-B | ReadProperty |  | X | 135-2001 | 1 | 2 | J | J
DS-RPM-A | ReadPropertyMultiple-A | ReadPropertyMultiple | X |  | 135-2001 | 1 | 2 | J | J
DS-RPM-B | ReadPropertyMultiple-B | ReadPropertyMultiple |  | X | 135-2001 | 1 | 2 |  | J
DS-RPC-A | ReadPropertyConditional-A | ReadPropertyConditional | X |  | 135-2001 entfernt in 135-2012
DS-RPC-B | ReadPropertyConditional-B | ReadPropertyConditional |  | X | 135-2001 entfernt in 135-2012
DS-WP-A | WriteProperty-A | WriteProperty | X |  | 135-2001 | 1 | 2 | J | J
DS-WP-B | WriteProperty-B | WriteProperty |  | X | 135-2001 | 1 | 2 |  | J
DS-WPM-A | WritePropertyMultiple-A | WritePropertyMultiple | X |  | 135-2001 | 1 | 2 | J
DS-WPM-B | WritePropertyMultiple-B | WritePropertyMultiple |  | X | 135-2001 | 1 | 2 |  | J
DS-COV-A | ChangeofValue-A | SubscribeCOV | X |  | 135-2001 | 1 | 2 | J | J
|  | ConfirmedCOVNotification |  | X
|  | UnconfirmedCOVNotification |  | X
DS-COV-B | ChangeofValue-B | SubscribeCOV |  | X | 135-2001 | 1 | 2 |  | J
| ChangeofValue-B | ConfirmedCOVNotification | X
| ChangeofValue-B | UnconfirmedCOVNotification | X
DS-COVP-A | ChangeofValueProperty-A | SubscribeCOVProperty | X |  | 135-2001 | 1 | 2 | J
| ChangeofValueProperty-A | ConfirmedCOVNotification |  | X | 135-2001
| ChangeofValueProperty-A | UnconfirmedCOVNotification |  | X | 135-2001
DS-COVP-B | ChangeofValueProperty-B | SubscribeCOVProperty |  | X | 135-2001 | 1 | 2 |  | J
| ChangeofValueProperty-B | ConfirmedCOVNotification | X |  | 135-2001
| ChangeofValueProperty-B | UnconfirmedCOVNotification | X |  | 135-2001
DS-COVU-A | ChangeofValue-Unsolicited-A | UnconfirmedCOVNotification |  | X | 135-2001 | 1 | 2
DS-COVU-B | ChangeofValue-Unsolicited-B | UnconfirmedCOVNotification | X |  | 135-2001 | 1 | 2
DS-V-A | View - A | ReadProperty | X |  | 135-2008 Add l | 1 | 9
DS-AV-A | Advanced View - A | ReadProperty | X |  | 135-2008 Add l | 1 | 9 | J
DS-M-A | Modify - A | WriteProperty | X |  | 135-2008 Add l | 1 | 9
DS-AM-A | Advanced Modify - A | WriteProperty | X |  | 135-2008 Add l | 1 | 9 | J
DS-WG-A | WriteGroup-A | WriteGroup | X |  | 135-2010 Add aa | 1 | 14
DS-WG-I-B | WriteGroup-Internal-B | WriteGroup |  | X | 135-2010 Add aa | 1 | 14
DS-WG-E-B | WriteGroup-Extenal-B | WriteGroup |  | X | 135-2010 Add aa | 1 | 14
|  | WriteProperty | X
Alarm and Event Management BIBBs (Alarm- und Ereignisverarbeitung)
AE-N-A | Notification-A | ConfirmedEventNotification |  | X | 135-2001 | 1 | 2 | J
|  | UnconfirmedEventNotification |  | X | 135-2001 |  | #VALUE!
AE-N-I-B | Notification Internal-B | ConfirmedEventNotification | X |  | 135-2001 | 1 | 2 |  | J
| Notification Internal-B | UnconfirmedEventNotification | X |  | 135-2001 |  | #VALUE!
AE-N-E-B | Notification External-B |  | X |  | 135-2001 | 1 | 2 |  | J
AE-ACK-A | ACK-A | AcknowledgeAlarm | X |  | 135-2001 | 1 | 2 | J
AE-ACK-B | ACK-B | AcknowledgeAlarm |  | X | 135-2001 | 1 | 2 |  | J
AE-ASUM-A | Alarm Summary-A | GetAlarmSummary | X |  | 135-2001 (abgekündigt gemäß 135-2008 Add. l) | 1 | 2
AE-ASUM-B | Alarm Summary-B | GetAlarmSummary |  | X | 135-2001 | 1 | 2 |  | J
AE-ESUM-A | Enrollment Summary-A | GetEnrollmentSummary | X |  | 135-2001 (abgekündigt gemäß 135-2008 Add. l) | 1 | 2
AE-ESUM-B | Enrollment Summary-B | GetEnrollmentSummary |  | X | 135-2001 | 1 | 2 |  | J
AE-INFO-A | Information-A | GetEventInformation | X |  | 135-2001 (abgekündigt gemäß 135-2008 Add. l) | 1 | 2
AE-INFO-B | Information-B | GetEventInformation |  | X | 135-2001 | 1 | 2 |  | J
AE-LS-A | LifeSafety-A | LifeSafetyOperation | X |  | 135-2001 | 1 | 2
|  | ConfirmedEventNotification |  | X | 135-2004 Add d | 1 | 5
|  | UnconfirmedEventNotification |  | X |  |  | #VALUE!
|  | AcknowledgeAlarm | X |  |  |  | #VALUE!
AE-LS-B | LifeSafety-B | LifeSafetyOperation |  | X | 135-2001 | 1 | 2
|  | ConfirmedEventNotification | X |  | 135-2004 Add d | 1 | 5
|  | UnconfirmedEventNotification | X |  |  |  | #VALUE!
AE-VN-A | View Notifications - A | ConfirmedEventNotification |  | X | 135-2008 Add l | 1 | 9
|  | UnconfirmedEventNotification |  | X
AE-AVN-A | Advanced View Notifications - A | ConfirmedEventNotification |  | X | 135-2008 Add l | 1 | 9 | J
|  | UnconfirmedEventNotification |  | X | 135-2008 Add l
AE-VM-A | View and Modify - A | ReadProperty | X |  | 135-2008 Add l | 1 | 9
|  | WriteProperty | X |  | 135-2008 Add l
AE-AVM-A | Advanced View and Modify - A | CreateObject | X |  | 135-2008 Add l | 1 | 9 | J
|  | DeleteObject | X
|  | ReadProperty | X
|  | WriteProperty | X
AE-AS-A | Alarm Summary View - A | GetEventInformation | X |  | 135-2008 Add l | 1 | 9 | J
|  | GetEnrollmentSummary | X
|  | GetAlarmSummary | X
AE-ELV-A | Event Log View - A | ReadRange | X |  | 135-2008 Add l | 1 | 9
AE-ELVM-A | Event Log View and Modify - A | ReadRange | X |  | 135-2008 Add l | 1 | 9 | J
|  | ReadProperty | X |  |  |  | #VALUE!
|  | WriteProperty | X |  |  |  | #VALUE!
AE-EL-I-B | Event Log - Internal - B | ReadRange |  | X | 135-2008 Add l | 1 | 9 |  | J
AE-EL-E-B | Event Log - Extenal - B | ReadRange |  | X | 135-2008 Add l | 1 | 9 |  | J
|  | ConfirmedEventNotification |  | X |  |  | 9
|  | UnconfirmedEventNotification |  | X |  |  | #VALUE!
AE-NF-B | Notification Forwarder-B | ConfimedEventNotification | X | X | 135-2010 Add af | 1 | 13
|  | UnconfimedEventNotification | X | X
|  | AddListElement |  | X
|  | RemoveListElement |  | X
AE-NF-I-B | Notification Forwarder-Internal-B | ConfimedEventNotification | X |  | 135-2010 Add af | 1 | 13
|  | UnconfimedEventNotification | X
|  | AddListElement |  | X
|  | RemoveListElement |  | X
Scheduling BIBBs (Zeitplan- und Zeitprogrammaustausch)
SCHED-A | Scheduling-A |  | X |  | 135-2001 (abgekündigt gemäß 135-2008 Add. l) | 1 | 2
SCH-I-B | Scheduling-Internal-B |  |  |  | 135-2001 (Änderung 135-2008 Add. l) | 1 | 2 |  | J
SCH-E-B | Scheduling-External-B |  |  |  | 135-2001 (Änderung 135-2008 Add. l) | 1 | 2 |  | J
SCH-AVM-A | Scheduling-Advanced View Modify-A | CreateObject | X |  | 135-2008 Add l | 1 | 9 | J
|  | DeleteObject | X
|  | ReadProperty | X
|  | WriteProperty | X
SCH-VM-A | Scheduling-View Modify-A | ReadProperty | X |  | 135-2008 Add l | 1 | 9
|  | WriteProperty | X
SCH-WS-A | Scheduling-Weekly Schedule-A | ReadProperty | X |  | 135-2008 Add l | 1 | 9
|  | WriteProperty | X
SCH-WS-I-B | Scheduling-Weekly Schedule Internal-B | ReadProperty |  | X | 135-2008 Add l | 1 | 9
|  | WriteProperty |  | X
|  | TimeSynchronization |  | X
|  | UTCTimeSynchronization |  | X
SCH-R-B | Scheduling-Readable-B |  |  |  | 135-2008 Add l | 1 | 9
Trending BIBBs (Trendaufzeichnung)
T-VMT-A | Viewing and Modifying Trends-A | ReadRange | X |  | 135-2001 (abgekündigt gemäß 135-2008 Add. l) | 1 | 2
T-VMT-I-B | Viewing and Modifying Internal-B | ReadRange |  | X | 135-2001 | 1 | 2 |  | J
T-VMT-E-B | Viewing and Modifying External-B |  |  |  | 135-2001 | 1 | 2 |  | J
T-VMMV-A | Viewing and Modifying Multiple Values-A | ReadRange | X |  | 135-2004 Add b (abgekündigt gemäß 135-2008 Add. l) | 1 | 7
T-VMMV-I-B | Viewing and Modifying Multiple Values Internal-B | ReadRange |  | X | 135-2004 Add b | 1 | 7
T-VMMV-E-B | Viewing and Modifying Multiple Values External-B |  |  |  | 135-2004 Add b | 1 | 7
T-AMVR-A | Automated Multiple Value Retrieval-A | ConfirmedEventNotification |  | X | 135-2004 Add b | 1 | 7 | J
|  | UnconfirmedEventNotification |  | X | 135-2008 Add ag | 1 | 12
|  | ReadRange | X |  | 135-2004 Add b | 1 | 7
T-AMVR-B | Automated Multiple Value Retrieval-B | ConfirmedEventNotification | X |  | 135-2004 Add b | 1 | 7
|  | UnconfirmedEventNotification | X |  | 135-2008 Add ag | 1 | 12
|  | ReadRange |  | X | 135-2004 Add b | 1 | 7
T-V-A | Trending – View - A | ReadRange | X |  | 135-2008 Add l | 1 | 9
T-AVM-A | Trending-Advanced View and Modify-A | CreateObject | X |  | 135-2008 Add l | 1 | 9 | J
|  | DeleteObject | X
|  | ReadProperty | X
|  | ReadRange | X
|  | WriteProperty | X
T-A-A | Trending-Archival-A |  |  |  | 135-2008 Add l | 1 | 9 | J
T-ATR-A | Automated Trend Retrieval-A | ConfirmedEventNotification |  | X | 135-2001 | 1 | 2 | J
|  | UnconfirmedEventNotification |  | X | 135-2008 Add z | 1 | 11
|  | ReadRange | X |  | 135-2001 | 1 | 2
T-ATR-B | Automated Trend Retrieval-B | ConfirmedEventNotification | X |  | 135-2001 | 1 | 2 |  | J
|  | UnconfirmedEventNotification | X |  | 135-2008 Add z | 1 | 11
| Automated Trend Retrieval-B | ReadRange |  | X | 135-2001 | 1 | 2
Device and Network Management BIBBs (Geräte- und Netzwerk-Management)
Device Management DM
DM-DDB-A | Dynamic Device Binding-A | Who-Is | X |  | 135-2001 | 1 | 2 | J | J
| Dynamic Device Binding-A | I-Am |  | X
DM-DDB-B | Dynamic Device Binding-B | Who-Is |  | X | 135-2001 | 1 | 2 | J | J
| Dynamic Device Binding-B | I-Am | X |  | 135-2001 |  |  | X | X
DM-DOB-A | Dynamic Object Binding-A | Who-Has | X |  | 135-2001 | 1 | 2 | J
|  | I-Have |  | X | 135-2001 |  |  | X
DM-DOB-B | Dynamic Object Binding-B | Who-Has |  | X | 135-2001 | 1 | 2 | J | J
|  | I-Have | X |  | 135-2001 |  |  | X | X
DM-DCC-A | DeviceCommunicationControl-A | DeviceCommunicationControl | X |  | 135-2001 | 1 | 2 | J
DM-DCC-B | DeviceCommunicationControl-B | DeviceCommunicationControl |  | X | 135-2001 | 1 | 2 |  | J
DM-PT-A | Private Transfer-A | ConfirmedPrivateTransfer | X |  | 135-2001 enfernt im 135-2004 Add d
|  | UnconfirmedPrivateTransfer | X
DM-PT-B | Private Transfer-B | ConfirmedPrivateTransfer |  | X | 135-2001 enfernt im 135-2004 Add d
|  | UnconfirmedPrivateTransfer |  | X
DM-TM-A | Text Message-A | ConfirmedTextMessage | X |  | 135-2001 | 1 | 2
|  | UnconfirmedTextMessage | X
DM-TM-B | Text Message-B | ConfirmedTextMessage |  | X | 135-2001 | 1 | 2
|  | UnconfirmedTextMessage |  | X | 135-2001
DM-TS-A | TimeSynchronization-A | TimeSynchronization | X |  | 135-2001 | 1 | 2
DM-TS-B | TimeSynchronization-B | TimeSynchronization |  | X | 135-2001 | 1 | 2 |  | J
DM-UTC-A | UTCTimeSynchronization-A | UTCTimeSynchronization | X |  | 135-2001 | 1 | 2
DM-UTC-B | UTCTimeSynchronization-B | UTCTimeSynchronization |  | X | 135-2001 | 1 | 2 |  | J
DM-RD-A | ReinitializeDevice-A | ReinitializeDevice | X |  | 135-2001 | 1 | 2 | J
DM-RD-B | ReinitializeDevice-B | ReinitializeDevice |  | X | 135-2001 | 1 | 2 |  | J
DM-BR-A | Backup and Restore-A | AtomicReadFile | X |  | 135-2001 | 1 | 2 | J
|  | AtomicWriteFile | X
|  | CreateObject | X
|  | ReinitializeDevice | X
DM-BR-B | Backup and Restore-B | AtomicReadFile |  | X | 135-2001 | 1 | 2 |  | J
|  | AtomicWriteFile |  | X
|  | ReinitializeDevice |  | X
DM-R-A | Restart-A | UnconfirmedCOVNotification |  | X | 135-2001 | 1 | 2 | J
DM-R-B | Restart-B | UnconfirmedCOVNotification | X |  | 135-2001 | 1 | 2 |  | J
DM-LM-A | List Manipulation-A | AddListElement | X |  | 135-2001 | 1 | 2 | J
|  | RemoveListElement | X
DM-LM-B | List Manipulation-B | AddListElement |  | X | 135-2001 | 1 | 2 |  | J
| List Manipulation-B | RemoveListElement |  | X | 135-2001
DM-OCD-A | Object Creation and Deletion-A | CreateObject | X |  | 135-2001 | 1 | 2 | J
| Object Creation and Deletion-A | DeleteObject | X |  | 135-2001
DM-OCD-B | Object Creation and Deletion-B | CreateObject |  | X | 135-2001 | 1 | 2 |  | J
| Object Creation and Deletion-B | DeleteObject |  | X | 135-2001
DM-VT-A | Virtual Terminal-A | VT-Open | X |  | 135-2001 | 1 | 2
|  | VT-Close | X | X
|  | VT-Data | X | X
DM-VT-B | Virtual Terminal-B | VT-Open |  | X | 135-2001 | 1 | 2
|  | VT-Close | X | X | 135-2001
|  | VT-Data | X | X | 135-2001
DM-ANM-A | Automatic Network Mapping-A |  |  |  | 135-2008 Add l | 1 | 9 | J
DM-ADM-A | Automatic Device Mapping-A |  |  |  | 135-2008 Add l | 1 | 9 | J
DM-ATS-A | Automatic Time Synchronization-A | TimeSynchronization | X |  | 135-2008 Add l | 1 | 9 | J
|  | UTCTimeSynchronization | X
DM-MTS-A | Manual Time Synchronization-A | TimeSynchronization | X |  | 135-2008 Add l | 1 | 9 | J
|  | UTCTimeSynchronization | X
Network Management NM
NM-CE-A | Connection Establishment-A | Establish-Connection-To-Network | X |  | 135-2001 | 1 | 2
|  | Disconnect-Connection-To-Network | X
NM-CE-B | Connection Establishment-B | Establish-Connection-To-Network |  | X | 135-2001 | 1 | 2
|  | Disconnect-Connection-To-Network |  | X
NM-RC-A | Router Configuration-A | Who-Is-Router-To-Network | X |  | 135-2001 | 1 | 2
|  | I-Am-Router-To-Network |  | X
|  | I-Could-Be-Router-To-Network |  | X
|  | Initialize-Routing-Table | X
|  | Initialize-Routing-Table-Ack |  | X
NM-RC-B | Router Configuration-B | Who-Is-Router-To-Network | X | X | 135-2001 | 1 | 2
|  | I-Am-Router-To-Network | X | X
|  | Initialize-Routing-Table |  | X
|  | Initialize-Routing-Table-Ack | X
Network Security NS
NS-SD | Secure Device | Challenge-Request |  | X | 135-2008 Add g | 1 | 11
|  | Security-Payload | X | X
|  | Security-Response | X | X
|  | Request-Key-Update | X
|  | Update-Key-Set |  | X
|  | Update-Distribution-Key |  | X
|  | What-Is-Network-Number | X | X
|  | Network-Number-Is | X | X
NS-ED | Encrypted Device |  |  |  | 135-2008 Add g | 1 | 11
NS-MAD | Multi-Application Device |  |  |  | 135-2008 Add g | 1 | 11
NS-DMK-A | Device Master Key-A | Request-Master-Key |  | X | 135-2008 Add g | 1 | 11
|  | Set-Master-Key | X
NS-DMK-B | Device Master Key-B | Request-Master-Key | X |  | 135-2008 Add g | 1 | 11
|  | Set-Master-Key |  | X | 135-2008 Add g
NS-KS | Key Server | Request-Key-Update |  | X | 135-2008 Add g | 1 | 11
|  | Update-Key-Set | X
|  | Update-Distribution-Key | X
|  | Request-Master-Key |  | X
|  | Set-Master-Key | X
NS-TKS | Key Server | Request-Key-Update |  | X | 135-2008 Add g | 1 | 11
|  | Update-Key-Set | X
|  | Update-Distribution-Key | X
|  | Request-Master-Key |  | X
|  | Set-Master-Key | X
NS-SR | Secure Router |  |  |  | 135-2008 Add g | 1 | 11
NS-SP | Secure Proxy |  |  |  | 135-2008 Add g | 1 | 11
Segmentation capability
Zur Übertragung von Segmentierten Nachrichten geeignet / Fenstergröße
Für den Empfang von Segmentierten Nachrichten geeignet / Fenstergröße
Data Link Layer options
BACnet IP, (AnnexJ) | [7 empty] | J | J
BACnet IP, (AnnexJ), Foreign Device
ISO 8802-3, Ethernet (Clause 7)
ANSI/ATA 878.1, 2.5 Mb. ARCNET (Clause 8)
ANSI/ATA 878.1, RS-485 ARCNET (Clause 8), baud rate (s)
MS/TP master (Clause 9), baud rate (s)
MS/TP slave (Clause 9), baud rate (s)
Point-To-Point, EIA 232 (Clause 10), baud rate (s)
Point-To-Point, Modem (Clause 10), baud rate (s)
LonTalk, (Clause 11), medium
BACnet/ZigBee (ANNEX O)
Other
Device Address Binding
Is static device binding supported? (This is currently necessary for two-way communication with MS/TP slaves and certain other devices.)
Networking Options
Router, Clause 6
Annex H, BACnet Tunneling Router over IP
BACnet/IP Broadcast Management Device ( BBMD)
Does the BBMD support registration by Foreign Devices
Does the BBMD support network address translation?
Character Sets Supported
ANSI X3.4 |  |  |  |  | 135-2001 |  |  | J
IBM™/Microsoft™ DBCS |  |  |  |  | 135-2001
ISO8859- 1 |  |  |  |  | 135-2001 |  |  | J | J
ISO 10646 (UCS-2) |  |  |  |  | 135-2001
ISO 10646 (UCS-4) |  |  |  |  | 135-2001
JIS C 6226 |  |  |  |  | 135-2001
ISO 10646 (UTF-8) |  |  |  |  | 135-2004 Add. h |  |  | J | J
Network Security
Non-secure Device - is capable of operating without BACnet Network Security
Secure Device - is capable of using BACnet Network Security (NS-SD BIBB)
Multiple Application-Specific Keys:
Supports encryption (NS-ED BIBB)
Key Server (NS-KS BIBB)
Legende:
J | Anforderungen des AG
Keine Anforderung des AG, bzw. in den behandelten Device-Profilen nicht geforderte Objekte/Properties.
J | Zukünftige Anforderungen des AG
Note on A99: Marius Hartel: Addendum l to 135-2008: “This BIBB has been deprecated and is included solely for historical purposes. This BIBB should not be used whendescribing the functionality of BACnet devices.”
Note on A116: Marius Hartel: Addendum l to 135-2008: “This BIBB has been deprecated and is included solely for historical purposes. This BIBB should not be used whendescribing the functionality of BACnet devices.”
Note on I122: Marius Hartel: bedingt durch T-A-A Anforderung
Note on I135: Marius Hartel: bedingt durch T-A-A Anforderung
Note on J162: Dipl.-Ing. Marius Hartel: 15.06.2009: (GA+MBS) einer der beiden Dienste TS-B oder UTC-B muss unterstützt werden.
Note on J164: Dipl.-Ing. Marius Hartel: 15.06.2009: (GA+MBS) einer der beiden Dienste TS-B oder UTC-B muss unterstützt werden.
Note on I263: Marius Hartel: Nur für die Aufschaltung des Bestandes