## Specification
Position | Item | Description | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns A-C, please indicate "Yes". Otherwise, describe your special features in this column.
1 | General Requirements
1.1 | Electric vehicle Charging solar car port | Charger must be compatible with Combined Charging System (CCS) Level 2 (240V - AC) or Level 3 (480V – DC Fast charging) standard. Peak DC Fast-Charger with Rated power of 130kW.
1.2 | Car port conditions | The car port is to be erected in GIZ office Abuja, Nigeria. (Ground mount) Temperatures may vary between 23 °C and 40 °C and humidity up to 88 %. Wind speeds: max. 40 km/h Installation height is 40 - 300 m above sea level. All components must be designed accordingly!
1.4 | Basic design principles | The components offered must be fully functional and compatible with each other. All components and parts that are not explicitly mentioned in this document, but are necessary to ensure a faultless room layout, installation and professional operation must be offered by the bidder (except for parts that are explicitly excluded from the tender). Minimum battery capacity of 100 kWh. Minimum PV capacity of 30 kWp.
1.5 | Standards and norms | The standards mentioned here may also be offered by equivalent standards as long as they cover the same requirements.
2 | Photovolatic Modules
2.1 | Photovolatic Modules | PV modules with crystalline technology, N-type TOPCon or HJT (Bifacial cells) - minimum Output per module 605 Wp, tolerance 0 ± 5%, (Bifacial gain +15–25% with light-colored ground) - Certification for wind load up to minimum ≥ 2400 Pa(rear) and ≥ 5400Pa(front) snow. - Solar cells are embedded in an EVA (ethylene vinyl acetate) layer, anti-reflective coating, front cover made of specially tempered, highly transparent glass. - Framed with aluminium profile (anodised), Anti-corrosion (marine-grade anodized Al, ≥ 40mm), anti - LID. - Maximum Norminal Operating Cell Temperature (NOCT) ≤ 45 °C, Temperature Coefficient ≤ -0.28 %/°C - Module efficiency must be ≥ 23 %, under STC conditions (1000 W/m² irradiance, 25°C cell temperature, AM1.5 spectrum) - Pmax coefficient >-0.30%/°C - PID-free, anti-dust coating (selfcleaning optional), Weatherproof junction box (Min IP68) - min. 3.2mm AR-coated, anti-reflective, anti-LID - Maximum system voltage 1000V - MC4 connectors campatible with high grade UV protected cable by at least 6mm² - Documentation: English Solar cables and associated connectors are pre-assembled and already attached and connected to the module, so that no further connectors and cables are necessary to connect the modules to each other. Cable lengths must be sufficient so that the modules can be easily connected to each other. Minimum distance of 20m from PV system to allow for connection to car port and components
2.2 | Certifications and standards | The module complies with the following certifications: - IEC 61 215 : Terrestrial photovoltaic (PV) modules - Type qualification and type approval. - IEC 61 730 : Photovoltaic (PV) modules - safety qualification - IEC 62782 tested - IEC 62759-1 Packaging, delivery and transportation standard The tests are carried out by recognised testing laboratories according to ISO/IEC 17025. - EN 50380: Data sheet content standard. - EN 50521: Connector standard compliance for cabling between modules. - EN 50380: Data sheet content standard. - UL 61730: Safety qualification for North American markets. . Quality control and assurance processes in manufacturing are certified, and compliance with IEC 61215 and IEC 61730 The manufacturer of the solar modules can prove by a suitable certificate that a permanent quality control and assurance of the production processes takes place in his factory. It must be proven that the standards according to IEC 61215 and IEC 61730 are also adhered to in ongoing production. The certificate itself is issued by an accredited testing institute. The normative requirements IEC 60891 ; IEC 60904 ; IEC 61345 ; IEC 61701; IEC 61721; EN 50380 are fulfilled. CE Declaration of Conformity by the manufacturer is available. A confirmation by a conformity assessment body according to ISO/IEC 17021 is available. CE marking of the solar modules is available. The solar modules are marked accordingly. ISO 4180 Weatherproof junction box on the back of the module. The junction box must comply with at least IP 65 and the DIN VDE 0126-5 standard. The cabling between the modules with connectors complies with the EN 50521 standard. IEC 61215/61730, UL 61730, Salt Mist Corrosion (IEC 61701)
2.3 | Delivery | The modules must be packed in wooden boxes or equivalent. IEC 62759-1 shall be observed with regard to the delivery/shipping of the modules. Flash data for each module must be provided as a digital file. Warranty documentation must be provided
2.3 | Warranty | Linear performance guarantee 30-year (≥87% at End of Life) with maximum degradation coefficient of ≤-0.43%/year 15-year product warranty If the rated power of the modules is undershot within the guaranteed warranty period, the modules will be replaced free of charge at each installation site in Abuja, Nigeria.
2.4 | Please specify: | Brand name, model, type
Area of the cells (LxW) in mm
Dimensions of the module (LxWxD) in mm
Weight of module in kg
Maximum power (Pmax) W
Maximum voltage ( Vmax) V
Maximum current ( Ipmax) A
Maximum reverse current IR [A]
Short-circuit current (Isc) A
Open circuit voltage ( Voc) V
Temperature coefficient for current A/°C
Temperature coefficient for voltage V/°C
Temperature coefficient for power %/°C
Nominal cell operating temperature ( NOCT)
Maximum system voltage ( Vsmax )
Operating temperature ( Min- Max ) °C
Ambient temperature ( Min - Max ) °C
Current-voltage characteristics at 25°C and other temperatures and irradiation
2.5 | Please enclose with quotation: | Data sheet
Test certificates according to IEC 61215 and IEC 61730
Certificates according to ISO/IEC 17025
Accreditation of the test centre/institute or test centres (IEC 61215, IEC 61730 and ISO/IEC 17025) according to EN 45011 - 45013
CE declaration of conformity of the manufacturer
Confirmation that upon delivery of the modules, the flasher protocols showing the rated power of all delivered modules are presented and handed over.
Declaration or explicit confirmation regarding the replacement of the modules according to item 2.3.
Explanations on packaging and handling of the solar modules with reference to IEC 62759-1
2.6 | EL measurements | The results and images of the flash tests and electroluminescence measurements issued to the serial numbers of the panels shall be submitted. All documents and technical documentation submitted must be legible and easily recognisable. Flash Test Enforcement Inclusion of contract clauses: "100% flash test reports required before shipment. QR-linked flash reports for individual module Demand EL (electroluminescence) tests to detect microcracks. IV curve testing on-site after installation. All certfications must be present before Shipment.
3 | Structure
3.1 | PV Mounting Structure | The substructure made of aluminium or steel must support the modules and withstand the local weather conditions. It must be sufficiently protected against corrosion. It must be made in accordance with the number of panels (2.1 - above) Angle of inclination: [12-15]°. Concrete foundations on flat ground. Special anti-theft bolts and nuts to match the modules. Lightning protection and earthing
3.3 | Warranty | min. 10 years
3.4 | Please specify: | Brand name, model, type
Data sheet
Detailed description of the anti-theft screws and nuts
Technical description of the substructure
Description of the lightning protection
3.5 | In case of order, to be provided before delivery: | Sectional drawings of the profiles and elevations
Detailed drawings of fixings (interfaces, connections)
Assembly instructions in English
4 | Inverter
4.1. | Inverter | The following functions and specifications are fulfilled: - Minimum AC power 80 kW, - enables supply of consumers with 230/415 V AC; 3L+PE+N - charges the battery with an integrated MPPT charge controller with PV capacity - U-I generator diagnosis and integrated with: - Protective conductor monitoring - Reverse DC Connection Protection - Over-Temperature Protection - Grid Monitoring/Earthing fault Detection - DC/AC Surge protection; Type II - Insulation Monitoring - Internal integration of battery racks, BMS, EMS, and control systems - Must be capable to work on off-grid and ON grid mode(Hybrid) - Fully insulated IP65 cabinet for outdoor installation with anti-corrosion class C4 minimum
4.2. |  | - Operation Temperature Range 2 - 60℃ (45℃ > Derating) - Total Harmonic Distortion current <3%, ≥98% Efficiency - Packaging must ensure moisture protection and vibration resistance, and must be clearly marked with handling instructions (e.g., stacking limits, fragile indicators). - IEC 62759-1 shall be observed with regard to delivery and shipping requirements All components shall comply with relevant grid codes and safety standards (e.g., IEEE 1547, IEC 62116).
4.3. | Capacity | Continuous power Minimum: 80 kW System voltage Output voltage 230/415 V AC +/- 5% Output frequency 50 Hz Pure sine wave voltage Integrated MPP tracker, multi-stage charging technology with capacity of DC / AC-coupled solar-storage Adjustable end-of-charge voltages adjusted to the interconnecting solar modules Support grid/generator interconnection
4.4. |  | Input frequency 50Hz Hz; automat. Automatic recognition 50Hz DC/AC ratio ~ 2 DC Side Specifications Parameter Specification (Minimum) Suitable for Minimum PV Capacity.... 30 kWp DC Maximum Voltage......... 850 V DC MPPT Range...... 420 – 800 V DC Multi -MPPT tracker Equipped with DC combiner box Rated MPPT Current........ Minimum 180 A Efficiency............ ≥97% European Weighted Efficiency........ 96% Battery side Specifications (Minimum) Battery Voltage range.............250 - 900V Integrated self-developed BMS / EMS for flexibility Support RS 485/CAN/wifi/3G/4G communication
4.5. | Handling | Graphic LCD display or Menu-guided operation Serial interface RS-232, PC connection via USB. RS 485/CAN, support remote and mobile monitoring. Incl. PC software
4.6. | Power protection | Overcharge protection Reverse polarity protection of modules, for battery via fuses Deep discharge protection Short-circuit protection of load and module Reverse polarity protection via internal fuses Reverse current protection at night Overtemperature and overload protection Audible alarm PE connection
4.7. | Certifications and standards | It must comply with the following standards: EN-IEC 62040, EN-IEC 60335-2-29, EN-IEC 62109-1, EN 55014-1, EN 55014-2, EN-IEC 61000-3-2, IEC 61000-6-1, IEC 61000-6-2, IEC 61000-6-3, IEC 61727, IEC 62619, IEC 61000-6-2/4, IEC 62271-304,IEC 60721-3 Manufactured according to ISO 9001 and ISO 14001, IEC 62116, ISO 4180 CE compliant
| Warranty | min. 10 years
| Please specify: | Brand name, model, type
Data sheet
5 | Battery
| Lithium-ion-battery LFP Battery, 1C Rated (Battery Energy Storage System) - Modular LiFePO4 min. 100 kWh (each battery module min. 7.68kWh) | 8,000 cycles @STC(75% Residual Capacity, EOL) 90% DoD, Proof of conformity to IEC 60896-21/22 and IEC 61427, 62619, 63056 is required. Minimum Service life of 12years at 20°C (EUROBAT standard) Installation must comply with Standards and regulations for installation: DIN EN 50272-2 (safety regulations for battery rooms) Supplied with manufacturer-certified rack, fully labeled with manufacturer, type, model number, nominal voltage (V), nominal capacity (Ah/kWh), month/year of commissioning. Proof of quality assurance system according to ISO 9001 / ISO 14001 ISO 45001 occupational health and safety or equivalent certification Fully insulated, corrosion-free terminal Fully insulated 1P68 cabinet for outdoor installation with sufficient cooling system Fully insulated copper connectors and screw heads
Interconnection lead poles with torque 20 - 22 Nm Environmentally friendly, minimum. ≥ 98 % recyclable Energy efficiency ≥ 80%, charging efficiency min. 94% Ampere-hour efficiency ≥ 90%. Capacity Scalability: 150 kWh Self-discharge rate: ≤ 2-3%/month at 20°C Must support hot swap, No memory effect Pre-wired connections enabling plug-and-play deployment on-site Sufficiently large containers for electrolyte circulation Each cell/battery must have a factory serial number and is labelled with at least the following data: Manufacturer, type, model number, nominal voltage in V, nominal capacity in Ah/kWh, month and year of commissioning. Each cell/rack must have a factory serial number. Standard battery accessories comprising current cable kit, communication cable, parallel connectors, racks, breakers, fuses and protection devices etc - Packaging must ensure moisture protection and vibration resistance, and must be clearly marked with handling instructions (e.g., stacking limits, fragile indicators). - IEC 62759-1 shall be observed with regard to delivery and shipping requirements - must comply with IEC 62619, IEC62056, IEC 61000-6-2/4, ISO 4180 This item must be capable of being integrated and compatible with the inverter system and could be quoted as a single All in-one modular unit.
Charge regulator
Protection functions: Short-circuit proof Overload protection Overtemperature protection Lightning and overvoltage protection AC side Compliance with other VDE/IEC regulations (contact protection etc.) Compliance with EMC limits (electromagnetic compatibility) according to EN 50081 and EN 55014 Radio interference suppression (VHF) Output power control of the feed-in inverter (item 1.3) via frequency for overcharge protection of the battery Other normative requirements IEC 62093 ;DIN EN 5178 ; are fulfilled CE declaration of conformity by the manufacturer is available. Confirmation by a conformity assessment body in accordance with ISO/IEC 17021 is available. CE marking of the battery-charging inverter is available. The battery charging inverters are marked accordingly. Communication point if necessary Control cable (e.g. LIYCY paired 2x2x0.25 or comparable type) if necessary
6 | Cable
| Solar cables | minimum width of 6 mm² copper cable with double insulation for up to 1000V, type C2 (high flame resistance), AN3 (high UV resistance) Maximum permissible conductor temperature at least 90°C in continuous use. The standard EN 50618 is fulfilled. Please calculate cable lengths and diameters for a fully functional system operation. Solar DC wiring must be carried out in accordance with IEC 62930:2017. Solar cables shall be used from PV modules junction boxes up to converters incoming sections (MPPT) and must have the below listed minimum technical characteristics: · Maximum continuous operating temperature: 120 °C · Rated voltage (U0/U): 0,6/1 kV AC · Maximum DC voltage ≥ 1500 V DC · EPR insulated cables · UV resistant · Suitable for outdoor and underground installation
| DC Cables | Aluminium or Copper Please calculate cable lengths and diameters for a fully functional system operation. Solar DC wiring must be carried out in accordance with IEC 62930:2017.
| AC Flex Cables | Please calculate cable lengths and diameters for a fully functional system operation. The AC wiring must be carried out in accordance with NFC 15-100 and according to the technical specifications for the building.
| Empty conduits | Cable trays, flexible pipes and trunking according bidders calculation.
| MC4 Connectors or equivalent | DC Connector (MC4) Specifications: - Protection Class: IP68 (weatherproof for Nigeria’s humid conditions), 6 mm² Muilti-contact MC4 Plug (-/Female) and (+/Male) - Protection Type: UV-resistant, flame-retardant. Please calculate quantity and diameters for a fully functional system operation.
| Cable ties and insulation tape (pack) | UV-resistant cable ties in all necessary sizes and quantities.
| Accessories | Change over (150 A/415V) DC Breaker Surge Protective Device (SPD) Combiner box Molded Case Circuit Breakers (MCCB) AC Breaker PV Isolator ATS LV panel 1 HP Air Conditioner Please calculate each quantity and sizes for a fully functional system operation.
7 | Other components
| EV Charger | Charger should be compatible with Combined Charging System (CCS) Level 2 (240V - AC) or Level 3 (480V – DC Fast charging) standard. Peak DC Fast-Charger with Rated power of 130kW.
| Earthing system | All system components must be properly grounded. All work must be carried out in accordance with international and local electrical norms and standards. Devices must be installed following the manufacturer’s instructions for grounding equipment.
| Monitoring | User-friendly interface with intuitive web platform or mobile app. Data visualization via graphs, charts, and tables. Track daily, monthly, yearly, and total energy generation (kWh). Display real-time operating parameters (power, voltage, etc.). Access to historical data and trends. Configurable user access levels for owners, technicians, and maintenance staff.
8 | erased
9 | Documentation
| The following documentation, in English, must be supplied in electronic form for all components of the system after the order has been placed: | Assembly instructions for the entire system. Overview for an installer on site, showing which components are connected to each other and how. This overview also refers to the corresponding installation instructions and assembly instructions for the individual components.
Circuit document
Description of the components
Wiring diagrams
Assembly instructions, installation instructions
Commissioning instructions
Operating instructions
Maintenance instructions
Error analysis and troubleshooting suggestions in the event of a malfunction
All necessary import papers like certificates of origin, detailed component catalogue, SONCAP (for each item), packing list (indicating component HS codes and Country of Origin), proforma invoice and any other document as may be required for Cutoms clearance.
10 | Material Delivery CIF Lagos Seaport
All material must be delivered CIF Lagos Seaport latest 2 months after order.
Immediately after placing the order, all relevant customs documents, such as the delivery note, packing list and pro forma invoice, must be submitted so that GIZ can prepare for import. This import preparation can take several months. Therefore the loading onto the ship can start only after approval by GIZ. This will happen when all customs documents are ready. The bidder must therefore allow to store all the goods for several months before transport can begin in the country of manufacture. The offer must include 3 months of storage. The costs for each additional month (max. 4-12 months) must be specified as an option price. The storage period of 3 months will be part of the criteria for the evaluation. Please also note that the payment terms are linked to this.
| Please specify: | Dimensions (LxWxH), weight (kg) incl. packaging for sea shipment
10a | Material Delivery FCA Hamburg Seaport (optional)
All material must be delivered FCA Hamburg Seaport instead of CIF Lagos Seaport latest 2 months after order. The option can be offered. All bidders must offer CIF Lagos Seaport, as this is the only one used for evaluation.
10b | Customs clearance (by giz)
| Customs clearance (by giz) | Customs clearance will be done by giz.
10c | Domestic Material Transport (by giz)
| Domestic Material Transport (by giz) | Domestic transport will be done by giz. Please calculate 14 days after customs clearance.
10d | Material Delivery DDP Lagos (optional)
All material must be delivered DDP Lagos instead of CIF Lagos Seaport latest 2 months after order. Detailled address will be defined by giz. The option can be offered. All bidders must offer CIF Lagos Seaport, as this is the only one used for evaluation.
11 | Service on site
| Please enclose with the offer: | Ful system setup and Installation
Installation and commissioning of all components and the complete Solar car port System. The supplier shall install, carry out all related electrical works and supplying of all necessary electrical equipment for the proper operation of the supplied technological equipment. Installation and commissioning at NESP office must be conducted according to Nigeria electrical quality and safety norms and standards. At least a Nigerian certified solar technician should be in the team to perfom the solar installation and commissioning. Complete commissioning of the solar car port System incl. function tests and trial operation. The technical commissioning of the car port will include training on the operation of the solar EV charging System and its components.
Accessory Material for required adaptations (installation) will be specified in type and quantitiy after contract conclusion. Necessary preparation work before installation have to be considered and taken care of by the project. Please describe which preparation work should be provided: All installations and equipment will be inspected and their functionality will be tested. It will be visually checked for compliance with the technical specifications and approved quotation. The completeness of drawings, operation and maintenance manuals will be checked as well. Furthermore it will be verified that the operating personnel at each site are adequately trained. A test will be carried out to demonstrate that the PV-System can be operated according to the technical specifications under all available operating conditions. To allow also a remote inspection by a Consultant, photos and videos of the installation and the equipment have to be taken and send to GIZ for verification.
Documentation: All work steps will be documented in detail throughout the installation phase. The documentation will include the final (actual) wiring diagram of all components and the car port-System.
Indication of what kind of service can be provided (spare parts procurement, spare parts exchange, fault analysis with repair etc.)
The installation and training shall be completed latest 1 month after the announcement of the successful customs clearance by the giz. Domestic Material transport by giz, please calculate 14 days after the announcement to have all materials on site.
The bidder must include flight, accommodation, catering and domestic travel for its staff in its bid.
12 | Warranty
| min. 5 years | On the entire system and installation. Fully according to GIZ General Purchase Conditions (GPC) 2023. The claims arising from the product and system warranties apply in addition to the claims for defects in accordance with GIZ GPC 2023. For individual components, longer warranty periods apply if described.
| Place of validity | All guarantee and warranty conditions apply at the locations of the installed PV-Systems at Abuja in Nigeria. Even if the material was handed over at other locations.
| Guarantee assignment declarations | All warranties must be assigned to GIZ and project partners by declaration. This declaration must be signed and stamped by each manufacturer/Installer.
13 | Training (optional)
| Remote Traininig | 2 x 8 hours, to train users (car drivers) to use the EV charging station
| Present Training | 2 x 8 hours, to train users (car drivers) to use the EV charging station
14 | Maintenance (optional)
| 2 years after commissioning | 1 regular maintenance and support per year