## Technical specifications
Position | Item | Description | Quantity | Unit | Price | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns A-F, please indicate "Yes". Otherwise, describe your special features in this column.
1 | General Requirements | 2 Cold Rooms for Vegetable Processing Center at One Mile, Kabala, Koinadugu District, Sierra Leone
| Cold Storage | Two cold rooms with different temperature zones Cold Room 1: - Temperature 5°C (mainly for Cabbage, Carrot, Green beans) - Average storage time: 1 - 6 weeks - cool-down time for newly stored vegetables: max. 24 hours Cold Room 2: - Temperature 16 °C (mainly for Tomatos, Lettuce) - Average storage time 2 - 4 days - cool-down time for newly stored vegetables: max. 5 hours Both rooms shall have: - Access should be provided via a door. - Monoblock air conditioner - The cold room requires shelving. | 2 | cold rooms
| Site conditions | The plant is to be erected in rural landscape. Ambient average temperature is 30 °C Cold Room will be placed in an existing building Foundation is available The room has vents/windows and sufficient space for the planned cold storages
| Power grid | The Cold Storage is connected to an island grid powerd by a pv-battery-system with a genset as backup
| Basic design principles | The components offered must be fully functional and compatible with each other. All components and parts that are not explicitly mentioned in this document, but are necessary to ensure a faultless room layout, installation and professional operation must be offered by the bidder (except for parts that are explicitly excluded from the tender).
2 | Cold Room
| Construction | The 2 cold rooms should be designed as an enclosed space (preferably using sandwich panels) based on a modular kit system. Including a insulated floor. - approximate inside dimension (WxDxH): 4 x 2 x 2,10 m = approx. 16 m³ Access should be provided via a door. - Single hinged swing door, right-hinged (opening to the right), suitable for cold storage insulation requirements Clear opening width: approx. 800 mm Clear opening height: approx. 1,800 mm - A PVC strip curtain shall be installed directly behind the cold room door. The cold room requires shelving. - Aluminium shelving with 4 tiers for storage of vegetable boxes (each shelf shall have a minimum load capacity of 150 kg/m²), NSF-certified, Number 1: 1 × Shelf unit – appr. 3.75 m (length) × appr. 0.50 m (depth) × appr. 1.80 m (height) Number 2 and 3: 2 × Shelf units – appr. 1.10 m (length) × appr. 0.50 m (depth) × appr. 1.80 m (height) Number 4: 1 × Shelf unit – appr. 0.75 m (length) × appr. 0.50 m (depth) × appr. 1.80 m (height) Please note that the shelves size could differ depending on the dimensions of the cooling room. It is however important, that the shelves fit into the cooling room as indicated on the sketch provided further down. The cold room must be illuminated. Must be build up in an existing room with sufficient ventilation (fan has to be supplied, see below). | 2 | cold rooms
| Insulation | Heat transfer of walls and ceiling less than 0,25 [W/(m2K)] High-performance thermal insulation based on cyclopentane-blown foam panels or equivalent climate-friendly solution.
| Please specify: | Brand name, model, type
heat transfer in [W/(m2K)]
Dimensions of the room (LxWxD) in cm
insulation material
Operating temperature ( Min- Max ) °C
Ambient temperature ( Min - Max ) °C
| Please enclose with quotation: | Data sheet and manuals
Test certificates according to any standard (ISO/IEC etc.)
CE declaration of conformity of the manufacturer
3 | Air conditioner
| operating principal | Monobloc air conditioner | 2 | piece
| Performance | Both air conditioners for Cold Room 1 and 2 shall be of the same model and type, with identical specifications. Performance was sized based on the assumption of a daily exchange of goods of max. 300 kg per Cold Room Cooling capacity at 30°C ambient temperature - approx. 2200 Watt at 5°C cold room temperature - approx. 2800 Watt at 16°C cold room temperature
| Electrical Rating | operating voltage 230V 1-phase electrical power in the range between 900 and 1100 Watt
| Refrigerant | Propane (R290)
| Other specifications | Wall mounted - particular designed for cold rooms - including humidifier - door contacts - Automatic restart after blackout - Optimized for operation with a solar power supply. (including possible connection to the Powerbank) - Remote monitoring including control functions (tempreature etc.)
| Certifications and standards | CE compliant
| Please specify: | Brand name, model, type
Data sheet
4 | Electrical Connection
| Distribution Box | A distribution box has to be supplied Including protection devices (short circuit and residual current) and connection terminals Protection has to exceed max. current of air conditioner, considering possible start current | 1 | piece
| Power Cable | Cabeling (NYM-Cable) from distribution box to air conditioner (Average distance from Cold storages to the main distribution board 20 m) | 40 | meter
| Sensor Cable | Cable from the air conditioner to the battery bank for optimized solar operation (Average distance 25 m) | 50 | meter
| mounting material | for mounting cables on to walls
5 | Documentation
| The following documentation, in English, must be supplied in electronic form for all components of the system after the order has been placed: | Assembly instructions for the entire system. Overview for an installer on site, showing which components are connected to each other and how. This overview also refers to the corresponding installation instructions and assembly instructions for the individual components.
Description of the components
Wiring diagrams
Assembly instructions, installation instructions
Commissioning instructions
Operating instructions
Maintenance instructions
Error analysis and troubleshooting suggestions in the event of a malfunction
6 | Delivery
| Service | Shipment and Transportation of all Equipment to site at Koinadugu District Women Vegetable Farmers’ Cooperative 1 at One Mile in Kabala Town, Koinadugu District, Sierra Leone with a GPS Coordinate (9°34'14.8"N 11°33'18.6"W). , Manual offloading of the materials, safe storage of the material, removal of all waste, cleaning of the site. | 1 | piece
| Please specify: | Dimensions (LxWxH), weight (kg)
7 | Service on site
Services includes |  | Professional assembly of the cold rooms at the designated positions within the building, according to the layout and manufacturer’s instructions. This includes the following - the installation of the refrigeration unit, including condensate drainage, insulation sealing, and integration of control components. - Electrical connection of the air conditioner to the main distribution board and sensor cable to the powerbank, including all necessary protective devices, wiring, and circuit breakers, in accordance with European electrical installation standards. - System commissioning, including start-up, functional testing, calibration of temperature controls, and verification of system performance. | 1 | piece
The installation of refrigeration and air-conditioning systems using natural refrigerants requires special training and qualifications in order to avoid accidents. The supplier must therefore ensure that the installation of the cold room will be carried out only by qualified technical staff on site.
Necessary preparation work before installation have to be considered and taken care of by the project. Please describe which preparation work should be provided: All installations and equipment will be inspected and their functionality will be tested. It will be visually checked for compliance with the technical specifications and approved quotation. The completeness of drawings, operation and maintenance manuals will be checked as well. Furthermore it will be verified that the operating personnel at each site are adequately trained. A test will be carried out to demonstrate that the air conditioner can be operated according to the technical specifications under all available operating conditions. To allow also a remote inspection by a Consultant, fotos and videos of the installation and the equipment have to be taken and send to GIZ for verification.
Documentation: All work steps will be documented in detail throughout the installation phase. The documentation will include the final position of the cold room and components like wall fan etc. (As-built plan)
Indication of what kind of service can be provided (spare parts procurement, spare parts exchange, fault analysis with repair etc.)
Address of the service centre in charge:
8 | Warranty
| min. 2 years | For the cold room as a a standalone functional component Fully according to GIZ General Purchase Conditions 2021. For individual components, longer warranty periods apply if described.
| Guarantee assignment declarations | All warranties must be assigned to GIZ and project partners by declaration. This declaration must be signed and stamped by each manufacturer.
9 | Training
| On-Site training | Duration: 1 day (each day = 8 hours) Objective: To train the responsible person on site in the proper use of the cold room, including correct handling of individual products (e.g., lettuce, tomatoes), appropriate settings, and basic maintenance. Location: On-site, Kabala Town, Sierra Leone Language: English with a local Krio translator Participants: Approximately 3–6 persons Training Topics: Proper handling of products Basic maintenance of the cold room, including the handling of natural refrigerants Functions and features of the control unit Health and safety aspects Cleaning and hygiene Temperature control and monitoring | 4 | hours
10 | Location of the site, cold rooms and position of the shelves
| Site Location | The Koinadugu District Women Vegetable Farmers’ Cooperative1 is located at One Mile in Kabala Town, Koinadugu District, Sierra Leone with a GPS Coordinate (9°34'14.8"N 11°33'18.6"W).
| Position of the cold rooms and the power room | Position of the cold rooms and the power room
| Positions of the shelves | Positions of the shelves