## Specifications
Lot | Item | Description | Quantity in meters | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns A-D, please indicate "Yes". Otherwise, describe your special features in this column.
Distribution Network Cable Please see "Standard and Certifications for items 1-5" below.
1 | ABC XLPE cable 3x50 mm² + 1x50 mm²+1x16 mm² 500 m drums | ABC cable 3x50 mm² + 1x50 mm²+1x16 mm² XLPE insulated, UV resistant, concentric neutral, overhead cable (Aerial Bundled Cable - ABC) [Aluminium] - IEC 60228, NFC 33-209 - Fufill Minimum IEC 60502-1 standard for Low Voltage power distribution (0.4kV - 1kV) - Must meet Nigerian Industrial Standard (NIS) | 100000
2 | XLPE cable 3x50 mm² + 1x50 mm² (Armoured) Upriser 1 drum (must be divided into 10 equal parts) | 3x50 mm² + 1x50 mm² (Armoured) with Galvanized steel wires/steel tape with high mechanical strength for underground power distribution. - XLPE insulated for undergrpound power distribution - Fufill Minimum IEC 60502-1 standard for Low and midium Voltage Power distribution (0.4kV - 33kV) - Copper conductor for minimum class 2, - Must fufill IEC 60228 and Nigerian Industrial Standard (NIS) | 300
3 | XLPE cable 1x70 mm² | XLPE cable 1x70 mm², IEC 60502-2, IEC 60228, NFC 33-209 - Fufill Minimum IEC 60502-4 standard for midium Voltage Power distribution (1kV - 33kV) - Aluminium conductor for minimum class 2 - NESIS Regulation 2015 | 6000
4 | Single Phase-ABC XLPE cable 2x10 mm² | Single Phase-ABC cable 2x10 mm² XLPE insulated, UV resistant, concentric neutral, overhead cable (Aerial Bundled Cable - ABC) [Aluminium] - IEC 60228 - Fufill minimum , NFC 33-209, IEC 60502-1 standard for Low Voltage power distribution (0.4kV - 1kV), Nigerian Industrial Standard (NIS) - Dielectric strength: Cores must be designed to withstand without breakdown the application of 10 kV voltage during 1 minute. - Impulse withstand: Cores must be designed to withstand without breakdown a standard impulse voltage sequence 1.2/50µs of positive and negative polarity with a peak value equal to 20 kV. - Routine test: 4 kV/15 minutes | 120000
5 | Three Phase-ABC XLPE cable 4x16 mm²+1×16 mm² 1000-1500 m drums | Single Phase-ABC cable 4x16mm² XLPE insulated, UV resistant, concentric neutral, overhead cable (Aerial Bundled Cable - ABC) [Aluminium] - IEC 60228 - Fufill Minimum NFC 33-209, IEC 60502-1 standard for Low Voltage power distribution (0.4kV - 1kV) and Nigerian Indusrial Standard (NIS) - Dielectric strength: Cores must be designed to withstand without breakdown the application of 10 kV voltage during 1 minute. - Impulse withstand: Cores must be designed to withstand without breakdown a standard impulse voltage sequence 1.2/50µs of positive and negative polarity with a peak value equal to 20 kV. - Routine test: 4 kV/15 minutes | 16000
Standard and Certifications for items 1-5
| Standard and Certifications for items 1-5 | The item supplied must conform with the most recent relevant codes, standards, accident prevention regulations and legal regulations in addition to the specific codes mentioned. The International Electrotechnical Commission (IEC) standards and recommended international best practices as well as the applicable and be compliant with the applicable Laws of the Federal Republic of Nigeria; including but not limited to “The Nigerian Electricity Health and Safety Code, 2014”, “The Nigerian Electricity Supply and Installation Standards Regulation, 2015” and the “The Distribution Code, 2014” of the Nigerian Electricity Regulatory Commission (NERC) as well as the “The Nigerian Electrical Installations and Construction Guidelines Manual, Distribution Subsector, Volume 1, 2020” of the Nigerian Electricity Management Services Agency (NEMSA), must be fulfilled whether mentioned or not in the following document. In any case, the mentioned any regulations or standards approved by the mandate institution or agency in Nigeria prevail over any other standard as a compulsory requirements. In addition all items must comply and be in accordance with the Nigerian Indutsrial Standard (NIS) latest IEC or equivalent standard which must be stated together with a copy of standard specifications. NERC Mini-Grid Regulation – Nigeria NESIS Regulations 2015 - The strands of phase and neutral conductors must consist of hard drawn aluminium alloy according to IEC 60889. The aluminium strands used for the construction of phase and neutral conductors for bundles must have, before stranding, an ultimate tensile stress at least equal to 120 MPa. - Insulating sheath: The insulation sheath must consist of an extruded sheath of cross-linked polyethylene conforming to IEC 502 and must be black-coloured. It must easily be removed. Insulation XLPE thickness is 1.5 mm. - Maximum permissible temperatures The maximum permissible temperatures for the Conductor are as follow: 1. 90°C during normal operation, 2. 120°C under a short duration overload (a total 24 hours a year in separate periods of 3 hours at the most) 3. 250°C under multi-phase short circuit conditions
Distribution Network Cable Accessories
6 | Complete D-Iron bracket and shackle porcelain Insulator | Complete D-iron bracket and shackles fitted with Brown Porcelain Insulator, Hot dip galvanized brackets and pins according to BS EN ISO 1461 (or its equivalents), M16 Hex head deck bolt, washers, nuts and other accessories to support the installation on a 8.5 and 12m LV and HT pole etc - Hex Bolts must fit to minimum - Must fuffil IEC 60383 - Must compatibly support the installation of minimum aerial bundle cable size (3x50 mm² + 1x50 mm²+1x16 mm² ) - 75kN Min load line hardware capacity, The grooves of the porcelain insulator must be suitable for bare conductor and aerial bundle cable (3x50 mm² + 1x50 mm²+1x16 mm² & 4x16 mm²+1×16 mm² ) distribution network and service line customer connection cables - Low frequency dry flashover voltage 25 - 30kV, and Low frequency wet flashover voltage 25 - 30kV - Leakage distance minimum 70mm - Combined mechanical and electrical strength (75kN, 0.4kV - 1kV, 50Hz) - The security clip must be of phosphor bronze material and the split pins must be stainless steel. | 9600
| Standard and Certifications | The item supplied must conform with the most recent relevant codes, standards, accident prevention regulations and legal regulations. The International Electrotechnical Commission (IEC) standards and recommended international best practices as well as the applicable and be compliant with the applicable Laws of the Federal Republic of Nigeria; including but not limited to “The Nigerian Electricity Health and Safety Code, 2014”, “The Nigerian Electricity Supply and Installation Standards Regulation, 2015” and the “The Distribution Code, 2014” of the Nigerian Electricity Regulatory Commission (NERC) as well as the “The Nigerian Electrical Installations and Construction Guidelines Manual, Distribution Subsector, Volume 1, 2020” of the Nigerian Electricity Management Services Agency (NEMSA), must be fulfilled whether mentioned or not in the following document. In any case, the mentioned any regulations or standards approved by the mandate institution or agency in Nigeria prevail over any other standard as a compulsory requirements. In addition all items must comply and be in accordance with the Nigerian Indusrial Standard (NIS) latest IEC or equivalent standard which must be stated together with a copy of standard specifications. NERC Mini-Grid Regulation – Nigeria NESIS Regulations 2015 - Must fuffil IEC 60383-1, 60433, 60273 - Material must be according BS EN ISO 1461 (or its equivalents)
Storage at Place of Production and Material Delivery CIF Lagos, Nigeria Seaport
All material must be delivered CIF Lagos Seaport latest 3 months after order.
| Please specify: | Dimensions (LxWxH), weight (kg) incl. packaging for sea shipment
Immediately after placing the order, all relevant customs documents, such as the delivery note, packing list and pro forma invoice, must be submitted so that GIZ can prepare for import. This import preparation can take several months. Therefore the loading onto the ship can start only after approval by GIZ. This will happen when all customs documents are ready. The bidder must therefore allow to store all the goods for several months before transport can begin in the country of manufacture. The offer must include 3 months of storage. The costs for each additional month (max. 4-12 months) must be specified as an option price. The storage period of 3 months will be part of the criteria for the evaluation. Please also note that the payment terms are linked to this.
- The Supplier must ensure that adequate handling equipment is possible to unload the heaviest piece of equipment at the delivery location (Project site). All cases and boxes must be clearly and boldly marked and must be addressed to the delivery address. All parts must be suitably protected against corrosion, water, sand, heat, any adverse atmospheric conditions, shocks, impact, vibrations, etc. for later transport and storage. Equipment and materials for each project must be marked separately and all material must be delivered to minmum 9 - 10 project locations across the North Central/West, Southwest, and South East zones in Nigeria in secured wooden drum and wooding box packings for the disctribution network accessories. - Delivery Note must be signed in blue ink by the receiver and supplier and be submitted to the NESP and must be accompanied by clear photographs of the asset at the delivery point. Each photograph must clearly show the coordinates of the delivery location, date, and time of delivery. - Sample delivery note to be shared by the NESP must be printed in triplicate and distributed as follows: NESP, Mini-Grid Developer/State warehouse contact person (receiver) and Supplier/Delivery company.
Customs clearance (by giz)
| Customs clearance (by giz) | Customs clearance in Nigeria will be done by giz. All necessary import papers like certificates of origin, detailed component catalogue, SONCAP (for each item), packing list (indicating component HS codes and Country of Origin), proforma invoice, delivery note and other documents that may be required from the supplier for the Importation and Clearing via Nigeria Ports"
Material Delivery DDP Lagos (optional)
All material must be delivered DDP Lagos instead of CIF Lagos Seaport latest 4 months after order. Detailled address at Lagos will be provided by giz with the offer. The option can be offered. All bidders must offer CIF Lagos Seaport, as this is the only one used for evaluation.
Documentation
| The following documentation, in English, must be supplied in electronic form for all components of the system after the order has been placed: | Handling and Assembly instructions for the cables. Overview for the handling on site and the corresponding installation instructions and assembly instructions not limited to the following.
Datasheets
Description of the components/ratings
Wiring diagrams/instruction
Commissioning instructions
Handling instructions, length in meter or KM/drum for each project site
All necessary import papers like certificates of origin, detailed component catalogue, Pictorial Samples are required with the offers
Warranty
| min. 6 years | Product warranty for min. 6 years. Fully according to GIZ General Purchase Conditions (GPC) 2023 in the first two years after delivery. The claims arising from the product and system warranties apply in addition to the claims for defects in accordance with GIZ GPC 2023.
| Place of validity | All guarantee and warranty conditions apply free of charge DDP Lagos Nigeria.
| Guarantee assignment declarations | All warranties must be assigned to GIZ and project partners by declaration. This declaration must be signed and stamped by each manufacturer/supplier.