## Technical Specification _BOQ
Pos. | Specification | Quantity | Unit | Price per unit | Total price | Supplier Remarks In each line, confirmation/statement regarding deviation from specification, brand and model type information where possible
1 | CO2 Transcritical ejector refrigeration system | 1 | Unit |  | 0
1.1 | Refrigerant: CO2 (R744)
1.2 | Cooling capacity: approx. 60 kW
1.3 | Application: Supermarket refrigeration
1.4 | Configuration: Booster system with parallel compression and ejector operation
1.5 | Operating mode: Transcritical and subcritical modes
1.6 | Ejector technology: Integrated high-pressure ejectors for energy recovery and flash gas management
1.7 | Gas cooler bypass valve or equivalent for pressure optimization
1.8 | Flash tank or receiver for liquid/vapor separation
1.9 | Compressor type: Semi-hermetic reciprocating or scroll compressors
1.10 | Compressor stages: Two-stage (medium temperature + low temperature)
1.11 | Number of compressors: Configurable based on load (e.g., 2MT + 1 LT minimum)
1.12 | Capacity modulation: Via frequency inverter (VFD) and or digital modulation
1.13 | Oil management system: Integrated oil separator and return system
1.14 | Power supply: 400V-3-50Hz
1.15 | Integrated control panel with PLC-based logic
1.16 | Remote monitoring capability: Modbus TCP/IP or BACnet compatible
1.17 | Safety protection: HP/LP pressure switches, temperature sensors, motor protection, alarm indicates etc.
1.18 | MT suction temperature range: Approx. -5℃ to -10℃
1.19 | LT suction temperature range: Approx. -30℃ to -35℃
1.20 | Gas cooler outlet pressure control: Via variable fan control or high-pressure valve
1.21 | Flash tank pressure control: Ejector and or parallel compression system
1.22 | Compact and modular design for easy transport and installation
1.23 | Frame material: Powder-coated galvanized steel or equivalent corrosion-resistant structure
1.24 | Sound insulation: Panels to minimize noise level (target ≤ 65 dB(A) at 10 m)
1.25 | Piping and vessels rated for ≥ 130 bar design pressure
1.26 | Anti-vibration mounts included
1.27 | Assembling manual in English language
2 | Electric panel for CO2 transcritical ejector refrigeration system. | 1 | Unit |  | 0
2.1 | Electric panel for CO2 transcritical ejector refrigeration system.
2.2 | Controller class: Advanced
2.3 | Electrical supply: 400V-3-50Hz
2.4 | Short circuit current (lcc3): approx. 10 kA
2.5 | Configuration: Left
2.6 | Options: Light and 230V socket; Phases monitoring
2.3 | Pannel designed for appropriate neutral presence
3 | Gas cooler | 1 | Unit |  | 0
3.1 | Refrigerant: CO2 (R744)
3.2 | Application: Gas cooler for transcritical CO2 system
3.3 | Calculated heat rejection approx. 60 kW
3.4 | Ambient temperature (℃): 27.0
3.5 | CO2 inlet temperature (℃): approx. 90.0
3.6 | CO2 outlet temperature (℃): approx. 28.0
3.7 | CO2 pressure (bar): approx. 75.0
3.8 | CO2 pressure drop (kPa): approx. 36.0
3.9 | Power supply: 400V-3-50Hz
3.10 | Max. current per motor (A): 2
3.11 | Max. Sound power level (dBA): 90
3.12 | Corrosion resistant
3.13 | Heat exchanger type: Microchannel or equivalent
3.14 | Fan type: Preferably Electronically commutated (EC) axial fans
3.15 | Fan motor protection: IP54 or better
3.16 | Mounting: Anti-vibration mounts included
3.17 | Pipping connections: CO2 inlet/outlet connections suitable for high pressure piping
3.18 | Assembling manual in English language
4 | Refrigeration system for small cold room (6m2) | 1 | Unit |  | 0
4.1 | Refrigerant: CO2 (R744)
4.2 | Application: Suitable for use in transcritical or subcritical CO2 commercial refrigeration system
4.3 | To (℃): -4
4.4 | Power supply: 230V-1-50Hz or 400V-3-50Hz
4.5 | Minimum cooling capacity: 2.7 kW
4.6 | Required Temperature: MT zero 0℃ at 32℃ ambient temperatures
4.7 | Size (m2): 6.0
4.8 | Room height (m): 2.5
4.9 | Room designation: Vegetables
4.10 | Fans: Axial fans, low noise, IP54 protection or higher suitable for cold room use
4.11 | Defrosting: Electrical defrost with stainless steel heaters or hot gas defrost option
4.12 | Drip tray: Sloped and heated, made of stainless steel or corrosion resistant coated steel
4.13 | Air throw: Designed for uniform distribution in cold rooms
4.14 | Safety features: Integrated thermal overload protection on fans and heaters
4.15 | Accessories: Supplied with mounted brackets, fans guards, and drain connections
4.16 | Installation: Ceiling or wall mounted evaporators for cold room
4.17 | Assembling manual in English language
5 | Refrigeration system for small cold room (3m2) | 1 | Unit |  | 0
5.1 | Refrigerant: CO2 (R744)
5.2 | Application: Suitable for use in transcritical or subcritical CO2 commercial refrigeration system
5.3 | To (℃): -4
5.4 | Power supply: 230V-1-50Hz or 400V-3-50Hz
5.5 | Minimum cooling capacity: 1.5 kW
5.6 | Required temperature: MT zero (0℃) at 32℃ ambient temperature
5.7 | Size (m2): 3.0
5.8 | Room height (m): 2.0
5.9 | Room designation: Dairy
5.10 | Fans: Axial fans, low noise, IP54 protection or higher suitable for cold room use
5.11 | Defrosting: Electrical defrost with stainless steel heaters or hot gas defrost option
5.12 | Drip tray: Sloped and heated, made of stainless steel or corrosion resistant coated steel
5.13 | Air throw: Designed for uniform distribution in cold rooms
5.14 | Safety features: Integrated thermal overload protection on fans and heaters
5.15 | Accessories: Supplied with mounted brackets, fans guards, and drain connections
5.16 | Installation: Ceiling or wall mounted evaporators for cold room
5.17 | Assembling manual in English language
6 | Refrigerated display cabinet – dairy one | 4 | Unit |  | 0
6.1 | Refrigerant: CO2 (R744)
6.2 | To (℃): -4
6.3 | Temperature class: 3M1
6.4 | Power supply: 230V-1-50Hz
6.5 | Cooling capacity: around 4.0 kW
6.6 | Length (m): around 3.75 external
6.7 | Depth (m): around 0.9 external
6.8 | Cabinet height (m): around 2.0 external
6.9 | Designation: Dairy
6.10 | Shelves: 5
6.11 | Lighting on shelves and handrail
6.12 | Doors: No
6.13 | Assembling manual in English language
7 | Refrigerated display cabinet – dairy two | 2 | Unit |  | 0
7.1 | Refrigerant: CO2 (R744)
7.2 | To (℃): -3.5
7.3 | Temperature class: 3M1
7.4 | Power supply: 230V-1-50Hz
7.5 | Cooling capacity: around 0.8 kW
7.6 | Length (m): around 1.9 external
7.7 | Depth (m): around 0.9 external
7.8 | Cabinet height (m): around 2.0 external
7.9 | Designation: Dairy
7.10 | Shelves: 6
7.11 | Lighting on shelves and handrail
7.12 | Doors: Yes
7.13 | Assembling manual in English language
8 | Refrigerated display cabinet – fruit vegetables one | 1 | Unit |  | 0
8.1 | Refrigerant: CO2 (R744)
8.2 | To (℃): -4
8.3 | Temperature class: S3
8.4 | Power supply: 230V-1-50Hz
8.5 | Cooling capacity: around 2.0 kW
8.6 | Length (m): around 1.9 external
8.7 | Depth (m): around 0.9 external
8.8 | Height (m): around 2.0 external
8.9 | Designation: Fruits-Vegetables
8.10 | Shelves: 5
8.11 | Lighting on shelves and handrail
8.12 | Doors: No
8.13 | Assembling manual in English language
9 | Refrigerated display cabinet – fruit, vegetables two | 2 | Unit |  | 0
9.1 | Refrigerant: CO2 (R744)
9.2 | To (℃): -4
9.3 | Temperature class: S3
9.4 | Power supply: 230V-1-50Hz
9.5 | Cooling capacity: around 2.0 kW
9.6 | Length (m): around 3.75 external
9.7 | Depth (m): around 0.9 external
9.8 | Height (m): around 2.0 external
9.9 | Designation: Fruits-vegetables
9.10 | Shelves: 6
9.11 | Lighting on shelves and handrail
9.12 | Doors: No
9.13 | Assembling manual in English language
10 | Refrigerated display cabinet – cake | 1 | Unit |  | 0
10.1 | Refrigerant: CO2 (R744)
10.2 | Minimum To (℃): -3.0
10.3 | Temperature class: 3M1
10.4 | Power supply: 230V-1-50Hz
10.5 | Cooling Capacity: around 0.6 kW
10.6 | Length (m): around 2.5 external
10.7 | Height (m): around 1.2 external
10.8 | Depth (m): around 1.2 external
10.9 | Designation: Cake
10.10 | Cabinet lighting included
10.11 | Assembling manual in English language
11 | Freezer display cabinet – frozen foods | 1 | Unit |  | 0
11.1 | Refrigerant: CO2 (R744)
11.2 | Ti (°C): -22/-24
11.3 | To (°C): -29
11.4 | Temperature class: L1, L3
11.5 | Power supply: 230V-1-50Hz
11.6 | Cooling Capacity: around 2.0 kW
11.7 | Height (m): around 2.0 external
11.8 | Depth (m): around 1.0 external
11.9 | Length (m): around 4.0 external
11.10 | Application: Vertical multideck cabinet for frozen and deep-frozen food display
11.11 | Designation: Freezer
11.12 | Shelves: 5
11.13 | Cabinet lighting included
11.14 | Doors: Yes
11.15 | Assembling manual in English language
12 | Freezer display cabinet – pet food | 1 | Unit |  | 0
12.1 | Refrigerant: CO2 (R744)
12.2 | Ti (℃): -22/-24
12.3 | To (℃): -29
12.4 | Temperature class: L1, L3
12.5 | Power supply: 230V-1-50Hz
12.6 | Cooling Capacity: around 1 kW
12.7 | Length (m): around 1.5 external
12.8 | Depth (m): around 1.0 external
12.9 | Height (m): around 2.0 external
12.10 | Application: Vertical multideck cabinet for frozen and deep-frozen food display
12.11 | Designation: Freezer-pet food
12.12 | Shelves:5
12.13 | Cabinet lighting included
12.14 | Door: Yes
12.15 | Assembling manual in English language
13 | Freezer island – one | 1 | Unit |  | 0
13.1 | Refrigerant: CO2 (R744)
13.2 | Ti (℃): -22/-24
13.3 | To (℃): -32
13.4 | Temperature class: 3L1
13.5 | Power supply: 230V-1-50Hz
13.6 | Minimum Cooling Capacity: 1.10 KW
13.7 | Length (m): around 3.75 external
13.8 | Height(m): around 0.9 external
13.9 | Depth - external (m): around 2.0 external
13.10 | Access: Horizontal glass-lid freezer with sliding lids
13.11 | Designation: Freezer
13.12 | Cabinet lighting included
13.13 | Assembling manual in English language
14 | Freezer display cabinet – freezer two | 2 | Unit |  | 0
14.1 | Refrigerant: CO2 (R744)
14.2 | Ti (℃): -22/-24
14.3 | To (℃): -32
14.4 | Temperature class: 3L1
14.5 | Power supply: 230V-1-50Hz
14.6 | Minimum cooling capacity: 0.8 KW
14.7 | Length (m): around 2.5 external
14.8 | Height (m): around 0.9 external
14.9 | Depth (m): around 2.0 external
14.10 | Access: Horizontal glass-lid freezer with sliding lids
14.11 | Designation: Freezer
14.12 | Cabinet lighting included
14.13 | Assembling manual in English language
15 | Freezer display cabinet – freezer three | 1 | Unit |  | 0
15.1 | Refrigerant: CO2 (R744)
15.2 | Ti (℃): -22/-24
15.3 | To (℃): -32
15.4 | Temperature class: 3L1
15.5 | Power supply: 230V-1-50Hz
15.6 | Minimum cooling capacity: 0.5 KW
15.7 | Length (m): around 1.9 external
15.8 | Height (m): around 1.0 external
15.9 | Depth (m): around 2.0 external
15.10 | Access: Horizontal glass-lid freezer with sliding lids
15.11 | Designation: Freezer
15.12 | Cabinet lighting included
15.13 | Assembling manual in English language
16 | Hot serve over counter | 4 | Unit |  | 0
16.1 | Refrigerant: CO2 (R744)
16.2 | Ti (℃): 60 to 65
16.3 | Power supply: 230V-1-50Hz
16.4 | Hot case heaters: around 2.0 - 3.0 kW
16.5 | Length (m): around 3.75 external
16.6 | Height (m): around 1.2 external
16.7 | Depth (m): around 1.2 external
16.8 | Operating thermostat: Yes
16.9 | Safety thermostat: Yes
16.10 | Calibration thermostat: Yes
16.11 | Application: Hot food display
16.12 | Designation: Serve over counter
16.13 | Cabinet lighting included
16.14 | Assembling manual in English language
17 | Assembly materials | 1 | Package |  | 0
17.1 | All materials and substances necessary for assembly, installation and operation of the components mentioned under pos. 1-16 must be supplied. (incl. necessary instrumentation, condensate drainages and piping, within the limits of the installation area)
17.2 | Please add a full list of Materials incl. Single prices for each item to your offer.
18 | Spare parts and consumables for 2 years of operation | 1 | Package |  | 0
18.1 | Spare parts and consumables for 2 years of operation must be supplied.
18.2 | Please add a list of Materials incl. Single prices for each item to your offer.
19 | Total Material price EXW (Pos. 1-18) | Sum |  |  | 0
20 | Transport & Packaging FCA Suppliers premises (Europe) | 1 | Unit
20.1 | Transport and packaging cost, including creation of export documents. Price to be submitted as a lump sum for the complete shipment
20.2 | Optional: You can include an Option for delivery DAP Woolmatt Nakuru, Kenya in your offer. Please note that Options do not need to be offered. They are not part of the evaluation and should not be included in the final offer price
21 | Total price FCA incl. Transport (Pos. 19+20) | Sum |  |  | 0
22 | Supervision of decommissioning of old system | 1 | psch
Supervision of decommissioning of old R22 system and recovery of the old refrigerant.
23 | Installation and commissioning of centralized transcritical CO2 ejector refrigeration system at Woolmatt Nakuru, Kenya | 1 | psch
Assembly, installation and commissioning of the new centralized CO2 system incl. all components mentioned under pos. 1-16 and those necessary for a proper installation and operation.
24 | Training of operators and service technicians at Woolmatt Nakuru, Kenya | 1 | psch
Training of operators and technical servicing team by an international refrigeration expert.
25 | Total price (Pos. 21-24) | Sum |  |  | 0
26 | Please confirm the availability of a technical support hotline to help with questions regarding the operation or troubleshooting of the equipment for minimum the warranty period of 2 years. Any commissioning of services resulting from it shall be carried out by the end user and must not be included with your offer. Non-confirmation of this point might lead to exclusion of the offer.