## Specification
Position | Item | Description for all countries | Specific Mali A comprehensive technical quotation in PDF format, including all technical data sheets, must be submitted as PDF file. | Specific Niger A comprehensive technical quotation in PDF format, including all technical data sheets, must be submitted as PDF file. | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns A-E, please indicate "Yes". Otherwise, describe your special features in this column. Conformity of individual components with the technical specifications listed below must be proven with technical data sheets in PDF format.
1 | General Requirements
1.1 | Solar container solution | Container-based pre-installed system. The container will serve as a precabled technical room for the inverters, batteries, and management and distribution equipment. The container is used to house and install all technical equipment, except for the solar panels and the solar module structures, which will be installed on the roof of a Community Resilience Center (CRC) building. The PV module structures must be made of stainless aluminum incorporating anti-theft bolts and a solar field angle adjustment device in order to account for the slope of the CRC building roof and achieve the recommended optimal inclination. The technical equipment should be prepared by the bidder "ready to use" so that only the PV structure, the PV modules and the module cables to the container must be assembled on site. All other components must be installed and ready to use inside the container. | Modular interoperability must be ensured to the extent that adding one or more systems can correspondingly increase the performance of the overall system, see point 9. - Two containers / modules are necessary, each container should have the same set up - The PV modules and the support structures for the PV modules will be associated with the container for transport. For Mali: one location, two connected systems required | Modular interoperability must be ensured to the extent that adding one or more systems can correspondingly increase the performance of the overall system, see point 9. The PV modules and the support structures for the PV modules will be associated with the container for transport. For Niger: two locations, one system for each location
1.1.1 | Capacities | The proposed solution must be a container-based pre-installed system with | Two 6" containers, total capacity connected containers: solar field capacity min. 33 kWc inverter capacity of min. 30 kVA storage capacity of min. 60 kWh | Two 6" containers, each: solar field capacity min. 16.5 kWc inverter capacity of min. 15 kVA storage capacity of min. 30 kWh
1.1.2 | Container | - External dimensions of each container : 1.98 x 1.95 x 1.91 m (6 ft container) - The weight per system must be limited so that two systems can be transported in one 20" ISO container, including the support structure and PV modules - PV field tilt: Variation of 15° - 20° - Colour: RAL 9003, Standard White
1.2 | Countries where this solar container solution is deployed |  | Mali, region of Mopti | Niger (one system for region of Zinder and one for Tahoua)
1.3 | Power grid | The solar container solution must allow the supply of electrical loads at a voltage of 400 VAC (3W+1N+1PE)
1.4 | Basic design principles | The components of the proposed container solution must be fully functional and compatible with each other. All components and parts not explicitly mentioned in this document, but necessary to ensure a professional installation and flawless operation, must be provided by the bidder (except for parts explicitly excluded from the tender).
1.5 | The main components of the solar container solution | Container, PV Modules, PV Module Structure, Solar Charge Controller, Inverter or Inverter integrating the charge controller, Batteries, Monitoring System and electrical protection equipment.
1.6 | Standards and norms | The standards mentioned in this specification may also be offered by equivalent standards as long as they cover the same requirements.
1.7 | Quantity of container system | 2 systems of 15 kVA for Mali 2 systems of 15 kVA for Niger | completed to one system of 30kVA/33kWc/60kWh | 2 separate systems with each 15kVA/16,5kWc/30kWh
2 | Photovolatic Modules
2.1 | Power of the solar field |  | 33 kWc | 2 x 16,5 kWc
2.2 | Technical data of the module | PV modules with crystalline technology. Output per module min. 450 W, tolerance 0 - 5%. Certification for wind load in Sahel region. Solar cells are embedded in an EVA (ethylene vinyl acetate) layer, anti-reflective coating, front cover made of specially tempered, highly transparent glass. Framed with aluminium profile (anodised).
2.3 | Product Certification | The module complies with the following certifications: - IEC 61 215 : Terrestrial photovoltaic (PV) modules - Type qualification and type approval. - IEC 61 730 : Photovoltaic (PV) modules - safety qualification The tests are carried out by recognised testing laboratories according to ISO/IEC 17025. The manufacturer of the solar modules can prove by a suitable certificate that a permanent quality control and assurance of the production processes takes place in his factory. It must be proven that the standards according to IEC 61215 and IEC 61730 are also adhered to in ongoing production. The certificate itself is issued by an accredited testing institute. The normative requirements IEC 60891 ; IEC 60904 ; IEC 61345 ; IEC 61701; IEC 61721; EN 50380 are fulfilled. CE Declaration of Conformity by the manufacturer is available. A confirmation by a conformity assessment body according to ISO/IEC 17021 is available. CE marking of the solar modules is available. The solar modules are marked accordingly. Weatherproof junction box on the back of the module. The junction box must comply with at least IP 65 and the DIN VDE 0126-5 standard. The cabling between the modules with connectors complies with the EN 50521 standard.
2.4 | Delivery | All modules must be packed for transport inside the container, see point 1.1. Flash data for each module must be provided as a digital file.
2.5 | Power Guarantee | ≤1% Degradation in the first year, ≤0.4% Annual degradation over 30 years Product guarantee for at least 10 years
2.6 | Please specify: | Brand name, model, type
Area of the cells (LxW) in mm
Dimensions of the module (LxWxD) in mm
Weight of module in kg
Maximum power (Pmax) W
Maximum voltage ( Vmax) V
Maximum current ( Ipmax) A
Maximum reverse current IR [A]
Short-circuit current (Isc) A
Open circuit voltage ( Voc) V
Temperature coefficient for current A/°C
Temperature coefficient for voltage V/°C
Temperature coefficient for power %/°C
Nominal cell operating temperature ( NOCT)
Maximum system voltage ( Vsmax )
Operating temperature ( Min- Max ) °C
Ambient temperature ( Min - Max ) °C
Current-voltage characteristics at 25°C and other temperatures and irradiation
2.7 | Please enclose with quotation: | Data sheet
Test certificates according to IEC 61215 and IEC 61730
Certificates according to ISO/IEC 17025
Accreditation of the test centre/institute or test centres (IEC 61215, IEC 61730 and ISO/IEC 17025) according to EN 45011 - 45013
CE declaration of conformity of the manufacturer
Confirmation that upon delivery of the modules, the flasher protocols showing the rated power of all delivered modules are presented and handed over.
Declaration or explicit confirmation regarding the replacement of the modules according to item 2.3.
Explanations on packaging and handling of the solar modules with reference to IEC 62759-1
3 | Structure
3.1 | Structure | The substructure made of aluminium or stainless steel must support the modules and withstand the local weather conditions. It must be sufficiently protected against corrosion. See attached drawing "installation". Inclination angle of the PV module plane on the roofs of CRC buildings: 15 - 20° relative to the horizontal plane. The slope of the CRC buildings is 3% Special anti-theft bolts and nuts to match the modules. Lightning protection and earthing Roof-mounted integration structure with angle variation device | Mali, region of Mopti | Niger, region of Zinder and Tahoua
3.2 | Roof conditions | Metal roof with steel roof truss. Sufficient roof space is available for installing the solar field.
3.3 | Manufacturer Warranty | min. 10 years
3.4 | Please specify: | Brand name, model, type
Data sheet
Detailed description of the anti-theft screws and nuts
Technical description of the substructure
Description of the lightning protection
3.5 | In case of order, to be provided before delivery: | Sectional drawings of the profiles and elevations
Detailed drawings of fixings (interfaces, connections)
Assembly instructions in English and French
4 | Inverter
4.1 | PowerControl & PowerAssist | Yes
4.2 | Total inverter capacity |  | 30kVA | 2 x 15kVA
4.4 | System output voltage | 400 VAC (3W+1N+1PE)
4.5 | Inverter unit capacity | 5kVA
4.6 | Inverter unit | The following functions are fulfilled: - enables supply of consumers with 220 V AC - charges the battery with an integrated MPPT charge controller [Max. battery charge current : 70A]. - simultaneously allows connection to a generator or power grid - U-I generator diagnosis - Protective conductor monitoring - Max apparent feed-in power : 5 000 VA
4.7 | Capacity unit | Continuous power min. 5 000 VA System voltage 48 V Output voltage 220 V AC +/- 5% Output frequency 50/60 Hz Pure sine wave voltage Integrated MPP tracker, multi-stage charging technology Adjustable end-of-charge voltages badjusted to the interconnecting solar modules from position 2 and, if applicable, known consumer devices. Input voltage 187 - 265 V AC Input frequency 45 - 65 Hz; automat. Automatic recognition 50/60 Hz Maximum output fault current : 53A for 1s
4.8 | Standards | Safety : EN-IEC 60335-1, EN-IEC 60335-2-29, EN-IEC 62109-1, EN-IEC 62109-2, AS 62477.1:2016, AS/NZS.2:2020 Inc A1
4.9 |  | Emission, Immunity : EN 55014-1, EN 55014-2 EN-IEC 61000-3-2, EN-IEC 61000-3-3, IEC 61000-6-1, IEC 61000-6-2, IEC 61000-6-3
4.10 | Quantity of inverter/charger units |  | 2 x 3 (3 inverters per container/modul) | 3 (3 inverters per container/modul)
5 | SmartSolar Charge Controller with VE.Can interface
5.1 | SmartSolar Charge Controller | Charge controller with MPPT technology. Maximum self-consumption 1 W. Complies with EN 62109-1. Electrical efficiency >90% (at 5 to 120% nominal power). Possibility to connect a remote control / remote monitoring is available Protection category : IP43 (electronic components), IP22 (connection area) Battery voltage : 12/24/48 V Auto Select Rated charge current : Min 100A Operating temperature : -30 to +60 °C (full rated output up to 40 °C) Safety : EN/IEC 62109-1, UL 1741, CSA C22.2 VE.Can interface It is recommended to consider inverters that incorporate charge controllers, see point 4.6
5.2 | Certifications and standards | It must comply with the following standards: EN-IEC 60335-1, EN-IEC 60335-2-29, EN-IEC 62109-1, EN 55014-1, EN 55014-2, EN-IEC 61000-3-2, IEC 61000-6-1, IEC 61000-6-2, IEC 61000-6-3. Manufactured according to ISO 9001 and ISO 14001. CE compliant
6 | Monitoring system
6.1 | Monitoring system | User-friendly interface with intuitive web platform or mobile app. Data visualization via graphs, charts, and tables. Track daily, monthly, yearly, and total energy generation (kWh). Display real-time operating parameters (power, voltage, etc.). Access to historical data and trends. Configurable user access levels for owners, technicians, and maintenance staff.
6.2 | Quantity of Monitoring system | 1
7 | Battery
7.1 | Lithium-ion battery | More than 6,000 cycles at 25°C / Nominal capacity : Min 4 800 Ah Service life according to EUROBAT min. 12 years at 20°C Standards and regulations for installation: DIN EN 50272-2 (safety regulations for battery rooms) Reference standards and certificats (mandatory): CE, UN 38.3, IEC 62619 and IEC 62477. Further reference standards: IEC 63056, IEC 61000-6-2, IEC 61000-6-3. The battery must be supplied with its rack certified by the manufacturer. Proof of quality assurance system according to ISO 9001 / ISO 14001 ISO 45001 occupational health and safety or equivalent certification Fully insulated, corrosion-free lead terminal All pole penetrations must ensure complete electrolyte and gas tightness even when positive plate is growing Fully insulated copper connectors and screw heads Interconnection lead poles with torque 20 - 22 Nm Environmentally friendly, min. 98 % recyclable Energy efficiency > 80% Ampere-hour efficiency > 90% Self-discharge less than 2-3%/month at 20°C Operating temperature charging/discharging until min. 50°C No memory effect Sufficiently large containers for electrolyte circulation Each battery is labelled with at least the following data: Manufacturer, type, model number, nominal voltage in V, nominal capacity in Ah, month and year of commissioning. Each cell must have a factory serial number
7.2 | Battery unit quantity |  | 6 for each container / module | 6 for each container / module
8 | Cable
8.1 | Solar cables | 1x [10] mm² copper cable with double insulation for up to 1000V, type C2 (high flame resistance), AN3 (high UV resistance) Maximum permissible conductor temperature at least 90°C in continuous use. The standard EN 50618 is fulfilled. Please calculate required diameters accroding to cable lengths and for a fully functional system operation. Solar DC wiring must be carried out in accordance with IEC 62930:2017. The minimum distance between the solar field (on the roof of the CRC buildings) and the planned location for the installation of the container solutions is 50m
8.2 | DC Cables | [Aluminium / Copper] Please calculate cable lengths and diameters for a fully functional system operation. Solar DC wiring must be carried out in accordance with IEC 62930:2017. Note: The wiring must be done at the factory
8.3 | AC Cables | [Aluminium / Copper] Please calculate cable lengths and diameters for a fully functional system operation. The AC wiring must be carried out in accordance with NFC 15-100 and according to the technical specifications for the building. Note: The wiring must be done at the factory
8.4 | Empty conduits | PE cable conduits for burial, double wall (corrugated outside, smooth inside according to standard NF EN 50086-2-4)
8.5 | Cable ties | UV-resistant cable ties in all necessary sizes and quantities.
8.6 | Accessories | All accessories for proper fastening of the cables under the modules for the entire installation.
9 | Others
9.1 | Ventilation / cooling of the container | At a minimum, automatic air extractors equipped with air filters will be necessary to ensure the control and regulation of the internal temperature of the container solutions.
9.2 | Connection terminal solar systems with main electric system/installation of CRC | The connection of the terminals of the solar systems to the main electrical installation system of CRC will be done by AC cable (cross-section and calculation note to be provided by each supplier) in buried mode over a minimum distance to be considered of 100m
9.3 | Connection terminal for interconnection of modules | The interconnection of the PV modules and the DC cables of the 'PV field - Container inverter' link will be done through MC4 solar connectors.
9.4 | Connection of inverter/Charger units | The inverter/charger units must be connected to each other by RJ45 cables and powered by the batteries, thus forming a single three-phase storage system.
10 | Documentation
10.1 | The following documentation, in French, must be supplied in electronic form for all components of the system after the order has been placed: | Assembly instructions for the entire system. Overview for an installer on site, showing which components are connected to each other and how. This overview also refers to the corresponding installation instructions and assembly instructions for the individual components.
10.2 |  | Circuit document
10.3 |  | Description of the components
10.4 |  | Wiring diagrams
10.5 |  | Assembly instructions, installation instructions
10.6 |  | Commissioning instructions
10.7 |  | Operating instructions
10.8 |  | Maintenance instructions
10.9 |  | Error analysis and troubleshooting suggestions in the event of a malfunction
11 | Spare parts (per system)
11.1 | Solar modules |  | min. 8 PV modules | min. 4 PV modules
11.2 |  | Please specify:
11.3 | Components and equipment outside of the container | min. 5 % of all equipment outside the container - including all big and small items like rails, nuts, cables, screws.
11.4 |  | Please specify:
12 | Material Delivery
12.1 | Delivery | All material must be delivered CPT GIZ Country offices BAMAKO and NIAMEY latest four months after order. | GIZ-Office in Bamako, Mali | GIZ-Office in Niamey, Niger
12.2 | Please specify: | Dimensions of standard ISO container incl. packaging for sea and truck shipment. | 20" container | 20" container
12a | Customs clearance (by giz)
| Customs clearance (by giz) | Customs clearance will be done by giz.
13 | Warranty
13.1 | min. 2 years | On the entire system and installation. Fully according to GIZ General Purchase Conditions (GPC) 2023. The claims arising from the product and system warranties apply in addition to the claims for defects in accordance with GIZ GPC 2023. For individual components, longer warranty periods apply if described.
13.2 | Place of validity | All guarantee and warranty conditions apply at the locations of the installed PV-Systems. Even if the material was handed over at other locations. This applies only insofar as the locations of the installed systems are accessible. Otherwise, spare parts must be delivered to the nearest GIZ office and technical support must be provided remotely.
13.3 | Guarantee assignment declarations | All warranties must be assigned to GIZ and project partners by declaration. This declaration must be signed and stamped by each manufacturer.
14 | Training (optional)
14.1 | Remote traininig | Min. 2 days The manufacturer must provide a training for instruction on installation and operation for at least one expert designated by GIZ. Language French.