## Specification
Lot | Position | Item description | Minimum Requirements | Unit of Measurement (UoM) | Quantity | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns B-F, please indicate "Yes". Otherwise, describe your special features in this column. | Type of procedure | Source of price
1 | 1.1 | Heat meter | Accuracy class - not lower than сlass B or equivalent class according to applicable standards; Nominal diameter - DN150; Maximum operating pressure, bar - 16; Maximum operating temperature, °C - 130; Connection type - flanged; Measuring medium - water; Installation position - horizontal; Heat calculator power supply - battery. Maximum water flow rate, m³/h - up to 300; Nominal water flow rate, m³/h - up to 250; Transitional volumetric water flow rate, m³/h - not more than 12; Minimum volumetric water flow rate, m³/h - not more than 5.5; Sensitivity threshold, m³/h - not more than 2; Package includes: - heat energy calculator; - temperature transducer - 2 pcs.(matched pair); - DN150 flanged flow meter with pulse output; - externally mounted pulse transmitter module. Technical passport (product passport) / certificate of conformity Operating instructions / Installation manual in Ukrainian and/or English Standard EN 1434 and directive 2014/32/EU (MID) or equivalent | pcs | 1 |  |  | Internet research** | Request for commercial offers
1 | 1.2 | Turbine gas meter | Meter type - turbine; Measurement environment - natural gas; Connection type - flanged; Meter size - G400; Nominal diameter - DN100; Presence of pulse output - yes; HF sensor type: inductive; Digital interface type - RS232 or RS485; Accuracy class - 1.0; Sensitivity threshold Qtrs, m3/h - 0.02 (with a relative operating flow range of 1:20); Maximum operating pressure, bar - not less than 6.3; Gas flow rate, Qmax, m³/h - not less than 650; Gas flow rate, Qmin, m³/h - not more than 20; Standard - DSTU EN 12261. Technical passport (product passport) / certificate of conformity Operating instructions / Installation manual in Ukrainian and/or English Standard EN 1434 and directive 2014/32/EU (MID) or equivalent | pcs | 1 |  | Direct award | market lowest | market lowest
2 | 2.1 | Circuit breaker 100A 3-phase | Power circuit breaker; Design - molded case; Number of poles (phases) - 3 (3 phases); Rated current In, A - 100; Breaking capacity, kA - 15; Rated operating voltage Ue, V - 380/690 (AC 50 Hz); Tripping characteristic - D; Mechanical endurance, cycles - not less than 7000; Electrical endurance, cycles - not less than 2000; Ingress protection rating - not lower than IP20. Technical passport (product passport) / certificate of conformity Operating instructions / Installation manual in Ukrainian and/or English Standard EN 60947-2 or equivalent | pcs | 50 |  | Negotiated award with a competitive tender | market average | market average
2 | 2.2 | Circuit breaker 3P-63A Type D | Design - modular; Number of poles (phases) - 3 (3 phases); Rated current In, A - 63; Breaking capacity, kA - 6; Rated operating voltage Ue, V - 230/380 (AC 50 Hz); Tripping characteristic - D; Mechanical endurance, cycles - not less than 10000; Electrical endurance, cycles - not less than 8000; Ingress protection rating - not lower than IP20. Technical passport (product passport) / certificate of conformity Operating instructions / Installation manual in Ukrainian and/or English Standard EN 60947-2 or equivalent | pcs | 50 |  | Negotiated award without a competitive tender | market average | highest market price
2 | 2.3 | Circuit breaker 3P-63A Type С | Design - modular; Number of poles (phases) - 3 (3 phases); Rated current In, A - 63; Breaking capacity, kA - 6; Rated operating voltage Ue, V - 230/380 (AC 50 Hz); Tripping characteristic - C; Mechanical endurance, cycles - not less than 10000; Electrical endurance, cycles - not less than 8000; Ingress protection rating - not lower than IP20. Technical passport (product passport) / certificate of conformity Operating instructions / Installation manual in Ukrainian and/or English Standard EN 60947-2 or equivalent | pcs | 100 |  | Public invitation to tender (Open procedure) | market average | market average
3 | 3.1 | Vacuum circuit breaker 6 kV | Execution - stationary; Type of cell for circuit breaker installation - KSO; Rated voltage, kV - 6; Rated breaking current, kA - ​​31.5; Rated current, A - ​​1000; Distance between pole centers, mm - 210; Connection of control circuits - terminal; The drive is spring-motor; Motor for charging the spring mechanism - 220V (DC or AC); Electromagnetic closing - 220V (DC or AC); Independent tripping (trip coil) - 220V (DC or AC); Second independent tripping (second tripping coil) - no; Auxiliary status contacts - 4NO+4NC (standard); Undervoltage release - 220V (AC); Current tripping (de-shunting) 2*5A - yes; Mechanical interlock (stationary version) - MIU_1; Upper pole protective cover (for stationary version and Inter-pole distance 210mm) - yes; Rear pole protective cover (for stationary version and inter-pole distance 210mm) - yes; Cassette locking electromagnet - no; Circuit breaker position sensor on the cassette (2NC+2NO) - no; Mechanical endurance, cycles - not less than 28000; Electrical endurance at rated breaking current, cycles - not less than 90; Ingress protection rating - not lower than IP20; Operating temperature range, °C - -45°C to +55; Standard - EN IEC 62271-100:2022, EN 62271-1:2018 or equivalent. Technical passport (product passport) / certificate of conformity Operating instructions / Installation manual in Ukrainian and/or English | pcs | 5
| 3.2 | Cable 1 | Description of cable type - Medium-voltage, true three-core aluminium conductor, XLPE insulated, electrically screened and metallic-armoured underground power cable with common outer sheath; Rated voltage (between phase conductors) - 10 kV; Number of cores - 3; Core material - Aluminium; Cross-section of conductive cores - 120 mm²; Conductor class - Class 2; Insulation - XLPE; Inner sheath - extruded PVC or equivalent; Armour - steel tape armour or technically equivalent metal; Outer sheath - PVC or PE; Reference cable designation - NA2XSEBY 3×120 mm² or technically equivalent. Quality passport / Quality certificate / Certificate of conformity EN 50575 (CPR) / EN IEC 60228 / EN 60502-2 or IEC 60502-2 or equivalent | m | 300
4 | 4.1 | Cable 2 | Description of cable type - Low-voltage, four-core aluminium conductor, PVC insulated and PVC sheathed power cable for fixed distribution installation; Rated voltage (between phase conductors) - 1 kV; Number of cores - 4; Core material - Aluminum; Cross-section of conductive cores - 240 mm²; Conductor class - Class 2, stranded; Insulation - PVC; Outer sheath - PVC, suitable for fixed installation; Reference cable - NAYY 4×240 mm² or technically equivalent. Quality passport / Quality certificate / Certificate of conformity EN 50575 (CPR) / EN IEC 60228 / EN 60502-1 or IEC 60502-1 or equivalent | m | 400 |  | * Deviations from such approach are to be justified and documented. ** When internet sources are used for the purposes of determining estimated cost, the prices are to be taken "as it is" without need to deduct or add VAT.
4 | 4.2 | Cable 3 | Description of cable type - Low-voltage self-supporting isolated bundled overhead line comprising four factory-bundled insulated aluminium conductors with weather- and UV-resistant XLPE insulation; Rated voltage (between phase conductors) - 1 kV; Number of cores - 4; Core material - Aluminium; Cross-section of conductive cores - 120 mm²; Conductor class - Class 2; Insulation - black UV-resistant XLPE that does not spread combustion; Reference cable - NFA2X 4×120 mm², AsXSn 4×120 mm² or technically equivalent. Quality passport / Quality certificate / Certificate of conformity EN 50575 (CPR) / EN IEC 60228 / HD 626 S1:1996 or equivalent | m | 200
5 | 5.1 | Cable 4 | Description of cable type - Low-voltage, single-core copper conductor, XLPE insulated, halogen-free low-smoke power cable for fixed installation; Rated voltage (between phase conductors) - 1 kV; Number of cores - 1; Core material - Copper; Cross-section of conductive cores - 240 mm²; Conductor class - Class 2; Insulation - XLPE; Outer sheath - Halogen-free compound/ HFFR/ LSZH; Flame propagation - flame-retardant; Smoke emission - low smoke; Reference cable - N2XH-O 1×240 mm² or technically equivalent. Quality passport / Quality certificate / Certificate of conformity EN 50575 (CPR) / EN IEC 60228 / EN 60502-1 or IEC 60502-1 or equivalent | m | 700
5 | 5.2 | Cable 5 | Description of cable type - Low-voltage, single-core copper conductor, XLPE insulated, halogen-free low-smoke power cable for fixed installation; Rated voltage (between phase conductors) - 1 kV; Number of cores - 1; Core material - Copper; Cross-section of conductive cores - 70 mm²; Conductor class - Class 2; Insulation - XLPE (cross-linked polyethylene); Outer sheath - LSZH/ HFFR; Flame propagation - flame-retardant; Smoke emission - low smoke; Reference cable - N2XH-O 1×70 mm² or technically equivalent. Quality passport / Quality certificate / Certificate of conformity EN 50575 (CPR) / EN IEC 60228 / EN 60502-1 or IEC 60502-1 or equivalent | m | 100
6 | 6.1 | Cable 6 | Description of cable type - Low-voltage, four-core aluminium conductor, XLPE insulated, metallic-armoured underground power cable with common outer sheath; Rated voltage (between phase conductors) - 1 kV; Number of cores - 4; Core material - Aluminium; Cross-section of conductive cores - 240 mm²; Conductor class - Class 2; Insulation - XLPE; Inner sheath - extruded PVC or equivalent; Armour - galvanised steel tape or technically equivalent metal; Outer sheath - PVC or PE; Reference cable - NA2XBY 4×240 mm² or technically equivalent. Quality passport / Quality certificate / Certificate of conformity EN 50575 (CPR) / EN IEC 60228 / EN 60502-1 or IEC 60502-1 or equivalent | m | 620
6 | 6.2 | Cable 7 | Description of cable type - Medium-voltage, true three-core aluminium conductor, XLPE insulated, electrically screened and metallic-armoured underground power cable with common outer sheath; Rated voltage (between phase conductors) - 10 kV; Number of cores - 3; Core material - Aluminium; Cross-section of conductive cores - 240 mm²; Conductor class - Class 2; Insulation - XLPE; Insulation screen - semiconductive; Inner sheath - extruded PVC or equivalent; Armour - galvanised steel tape or technically equivalent metal; Outer sheath - PVC or PE; Reference cable - NA2XSEBY 3×240 mm² or technically equivalent. Quality passport / Quality certificate / Certificate of conformity EN 50575 (CPR) / EN IEC 60228 / EN 60502-2 or IEC 60502-2 or equivalent | m | 620
7 | 7.1 | Cable 8 | Description of cable type - Medium-voltage, true three-core aluminium conductor, XLPE insulated, electrically screened, metallic-armoured and radially and longitudinally watertight underground power cable with common moisture-resistant outer sheath; Rated voltage (between phase conductors) - 10 kV; Number of cores - 3; Core material - Aluminium; Cross-section of conductive cores - 240 mm²; Conductor class - Class 2; Insulation - XLPE; Metallic screen - copper wire/tape or equivalent metal; Longitudinal water blocking - required; Radial moisture protection - required; Armour - steel tape or technically equivalent metal; Outer sheath - PE or equivalent moisture-resistant fireproof compound; Reference cable - water-protected NA2XSEBY 3×240 mm² or technically equivalent. Quality passport / Quality certificate / Certificate of conformity EN 50575 (CPR) / EN IEC 60228 / EN 60502-2 or IEC 60502-2 or equivalent | m | 2350

## Delivery Plan
No. | Delivery address | Position (quantity for delivery, pcs)
| The delivery schedule contains only the location details. A detailed address will be provided for each location after order. | 1.1 | 1.2 | 2.1 | 2.2 | 2.3 | 3.1 | 3.2 | 4.1 | 4.2 | 5.1 | 5.2 | 6.1 | 6.2 | 7.1
1 | Monastyryshche, Cherkasy region | 1 | 1
2 | Sumy |  |  | 50 | 50 | 100
3 | Kropyvnytskyi | [5 empty] | 5 | 300
4 | Teplodar, Odesa region | [7 empty] | 400
5 | Novovolynsk, Volynskiy region | [8 empty] | 200
6 | Bila Tserkva, Kyiv region | [9 empty] | 700 | 100
7 | Shostka, Sumy region | [11 empty] | 620 | 620
8 | Chernihiv | [13 empty] | 2350
|  | 1 | 1 | 50 | 50 | 100 | 5 | 300 | 400 | 200 | 700 | 100 | 620 | 620 | 2350

## Overview
Lot | Position | Item description | Unit | Quantity
1 | 1.1 | Heat meter | pcs | 1
| 1.2 | Turbine gas meter | pcs | 1
2 | 2.1 | Circuit breaker 100A 3-phase | pcs | 50
| 2.2 | Circuit breaker 3P-63A Type D | pcs | 50
| 2.3 | Circuit breaker 3P-63A Type С | pcs | 100
3 | 3.1 | Vacuum circuit breaker 6 kV | pcs | 5
| 3.2 | Cable 1 | m | 300
4 | 4.1 | Cable 2 | m | 400
| 4.2 | Cable 3 | m | 200
5 | 5.1 | Cable 4 | m | 700
| 5.2 | Cable 5 | m | 100
6 | 6.1 | Cable 6 | m | 620
| 6.2 | Cable 7 | m | 620
7 | 7.1 | Cable 8 | m | 2350