## Spezifikation
| General Requirements (for all generators) | Specific Requirements |  |  | Remarks | Note
|  | 12 kVA | 300 kVA | 600 kVA | The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns A-E, please indicate "Yes". Otherwise, describe your special features in this column. | In case of product specific information please write your remarks as below: 12 kVA: _ _ __ 300 kVA: _ _ __
1.0 | Generator
| Fuel | Petrol | Diesel | Diesel
| weatherproof/soundproof hood | yes | water-cooled, soundproofed | water-cooled, soundproofed
| Exhaust system fully integrated (inside) | Robust design as a unit ready for operation mounted on a base frame, consisting of motor, generator, battery, tank and Control box and listed accessories. | With lockable, robust design as a unit ready for operation mounted on a base frame, consisting of motor, generator, battery, tank and separate Control box and listed accessories. | With lockable, robust design as a unit ready for operation mounted on a base frame, consisting of motor, generator, battery, tank and separate Control box and listed accessories.
Standards and references: all VDE, EN, DIN, ISO standards or specifications relevant to the product must be complied with. In particular, VDE 0100 Part 551/560, VDE 0108, DIN ISO 8528, DIN ISO 3046, EltBau VO as well as standards mentioned in the specification text and other standards must be applied. CE marking is available.
1.0.1 | PRIME POWER: in kVA (tolerance +10%) under the environmental conditions mentioned (Pos. 1.0.2) (Variable continuous power PRP according to DIN ISO 8528, 24 h under variable load, overload 10 % for 1 hour in 12 hours). | 12 kVA | 300 kVA | 600 kVA
1.0.2 | PARTICIPATION AND PURPOSE / Environmental conditions ambient temperature -25..-..+40°C Insulation must be suitable for continental, steppe / Ukrainian climate. Up to 500 m altitude.
1.0.3 | Apart from the manufacturer's logo, no additional advertising may be visible on the generator. (In the event of non-compliance, the costs of removal will be charged.) Exceptions are only permitted with the written consent of GIZ.
1.0.4 | Generator type (make, model, type, designation etc.)
1.0.5 | CE declaration of conformity by the manufacturer is available. Please attach to the offer.
1.0.6 | CE marking of aggregate, generator and engine available. Products are marked.
1.1 | STRUCTURE
1.1.1 | Stationary design | mobile design with wheels | Stationary design | Stationary design
1.1.2 |  |  | Base frame made of welded sectional steel, torsion-resistant with lifting eyes suitable for loading the unit. | Base frame made of welded sectional steel, torsion-resistant with lifting eyes suitable for loading the unit.
1.2 | MOTOR, standards and benchmarks: ISO 3046, DIN 6271, BS 5514
1.2.1 | Engine type: fuel direct injection, pressure lubrication, fuel feed pump | Petrol | Diesel | Diesel
1.2.2 | Number of cylinders: no specification
1.2.3 | Make specification: No
1.2.4 | Speed: | 1500 rpm or 3000 rpm | 1500 rpm | 1500 rpm
1.2.5 | Speed control: mechanical
1.2.6 | Cooling: water-cooled, designed for an ambient temperature according to item 1.0.2. The proof of sufficient dimensioning of the cooling system under the mentioned environmental conditions must be kept separately.
1.2.7 | Alternator, battery charging system: integrated, 12 V / 24 V
1.2.8 | Starter, electric start: integrated, 12 V / 24 V
1.2.9 | Starter battery mounted on the unit with cover, 12V / 24 V, dry pre-charged
1.2.10 | Tank: Tank in base frame, with optical filling level indicator and/or see measuring instruments, tank capacity sufficient for at least 10 operating hours at 75 % load
Please specify :
1.2.11 | Engine make, model, type and kWelectric (efficiency losses and self consumption for cooling and operation already deducted)
1.3 | GENERATOR Standards and reference values : VDE 0530, BS 4999, UTE NFnC 51.111, IEC 34.1, NEMA MG 21.
1.3.1 | generator according to VDE 0530, internal pole machine with damper winding, self-regulating, self-excited | 1-phase | 1- or 3-phase | 1- or 3-phase
1.3.2 | Voltage stiffness: max 5 %.
1.3.3 | Output voltage: | 230 V alternating current | 230 V alternating current / 400 V three-phase current | 230 V alternating current / 400 V three-phase current
1.3.4 | Frequency: 50 Hz
1.3.5 | Power factor: cos phi 0.8
1.3.6 | Power rating for insulation class: F
1.3.7 | Insulation suitable for continental, steppe / Ukrainian climate
1.3.8 | Radio interference suppression level acc. to VDE 0875 "N"
1.3.9 | Protection class according to DIN 40050: IP 24
1.3.10 | classification according to DIN ISO 8528 | G1 | G3 | G3
Please specify :
1.3.11 | Generator and Alternator make, model, type and efficiency
1.4 | EXHAUST SYSTEM, SOUND INSULATION
1.4.1 | Weather and noise protection hood. Sound pressure level 70 dB(A) / 80 dB(A) in 7m or lower | Weather and noise protection hood incl. exhaust silencer, exhaust system fully integrated (inside), completely mounted ready for operation. | Weather and noise protection hood incl. exhaust silencer, exhaust system fully integrated (inside), completely mounted ready for operation (window for the control display). | Weather and noise protection hood incl. exhaust silencer, exhaust system fully integrated (inside), completely mounted ready for operation (window for the control display).
Please specify:
1.4.2 | Sound power level [dB (A)]
1.5 | SWITCHGEAR / CONTROL / MEASURING INSTRUMENTS / OTHER
1.5.1 | Displays: - Current intensities (switchable to single phases), simple and compound voltages, frequency, active, reactive and apparent power, power factor - fuel level, oil pressure, coolant temperature, battery voltage - Operating hours counter, time switch Start". - Multilingualism of the display instruments | not required | required | required
1.5.2 | Errors and alarm messages - min/max generator voltage, min/max generator frequency, overload and/or short circuit - Low fuel level, oil pressure, coolant temperature, min/max battery voltage, charging generator fault, - Malfunction: General, false start, emergency stop - General warning light
1.5.3 | Protective devices: - Engine protection devices (oil pressure, water temperature, overspeed), - Generator circuit breaker, - Thermal-magnetic overload protection, - Protection of instruments, displays, - Emergency stop button
1.5.4 | Operation: Emergency stop button Prepared and able for later installation of ATS automatic start | Electric start and stop button | Manual start and stop button | Manual start and stop button
1.5.5 | Connections: | not required | USB port, RS 485 | USB port, RS 485
1.5.6 | Display | not required | Multilingualism of the display instruments | Multilingualism of the display instruments
1.5.7 | Switchgear mounted vibration-free on the base frame of the unit
1.5.8 | Inscription of the generator, the control panel, etc.. in English or Ukrainian if possible.
1.5.9 | Optional: automatic preheating system for the generator system Please specify the additional price per unit and type of system (including datasheet) Note: Evaluation will be excecuted without considering any option.
2. | DOCUMENTATION
2.1 | Operating instructions, installation/commissioning manual, repair instructions (with troubleshooting instructions - WORKSHOP MANUAL), spare parts catalogue for generators as well as in detail for engine, generator; circuit diagram - in English and - if additionally possible - in Ukrainian language.
3. | DIMENSIONS, WEIGHT
3.1 | Dimensions (LxWxH), weight (kg), unfilled, incl. packaging for shipping by truck
4. | ON-SITE SERVICE
4.1 | Address of the service / contact details