## Spezifikation
Position | Item | Minimum requirement for each battery system 18 Systems in total (basic offer) | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns A-C, please indicate "Yes". Otherwise, describe your special features in this column.
1 | General Requirements
1.1 | Battery systems | System size at least min. 60 kWh Battery systems incl. - LiFePo-Batteries - Battery storage - Grid connection - Inverter
1.2 | Site conditions | All battery systems will be to be erected in Ukraine and must fit to Ukrainian weather conditions. All components must be designed accordingly!
1.3 | Power grid | It is intended to connect the systems to the local public grid. The design of the system and the inverters should be such that a later grid connection is possible.
1.4 | Basic design principles | The components offered must be fully functional and compatible with each other. All components and parts that are not explicitly mentioned in this document, but are necessary to ensure a faultless layout, installation and professional operation must be offered by the bidder (except for parts that are explicitly excluded from the tender).
1.5 | Standards and norms | The standards mentioned here may also be offered by equivalent standards as long as they cover the same requirements.
2 | erased
3 | erased
4 | Inverter
| One Inverter | The following functions are fulfilled: - enables supply of consumers with 230 V AC - 3 phase system requested - charges the battery with an integrated MPPT charge controller. - simultaneously allows connection to a generator or power grid - U-I generator diagnosis - Protective conductor monitoring
| Capacity of inverter | Continuous power min. 22000 VA inverter High voltage system (HV) Output voltage 230 V AC +/- 5% Output frequency 50/60 Hz Pure sine wave voltage Integrated 2 MPP tracker, multi-stage charging technology MPP voltage range up to 1200 V starting voltage up to 220 V inverter nominal voltage range has to be specified in the offer, a range is not specified.
| Handling | Graphic LCD display or or simply connect it to a standard mobile device Menu-guided operation Serial interface RS-232, PC connection via USB, (WIFI optional) Incl. PC software
| Power protection | Overcharge protection Reverse polarity protection of modules, for battery via fuses Deep discharge protection Short-circuit protection of load and module Reverse polarity protection via internal fuses Reverse current protection at night Overtemperature and overload protection Anti-islanding protection Audible alarm PE connection
| Certifications and standards | It must comply with the following standards: IEC 60947-6-1:2005, DSTU IEC 60947-6-1:2007 IDT or similar Manufactured according to ISO 9001 and ISO 14001. CE compliant
| Warranty | min. 5 years
| Please specify: | Brand name, model, type
Data sheet
5 | Battery
| LiFePO4-battery system min 60 kWh Energy and min. 55 kWh usable capacity Peak output power 15-20kW/60s Protection class min. IP20 Operating temperature -10°C to 50°C Storage temperature 0°C to 35°C Natural cooling without fan IEC62619 certificate CE UL1973 UL 9540A | Number of single batteries: 12 Module energy (kWh) of each battery: min. 5 kWh Charge/Discharge Current (A): min. 50 A Depth of discharge(%): Not lower than 0.9 Min. 3,000 cycles @50% DoD, 20°C / 1,500 cycles @80% DoD, 20°C Proof of conformity to IEC 60896-21/22, UL1973, UL9540A is required. Service life according to EUROBAT min. 10 years at 20°C Standards and regulations for installation: DIN EN 50272-2 (safety regulations for battery rooms) Installation location: Rack mounting in standard 19-inch rack. The battery must be supplied with its rack certified by the manufacturer. Proof of quality assurance system according to ISO 9001 / ISO 14001 ISO 45001 occupational health and safety or equivalent certification Fully insulated, corrosion-free lead terminal All pole penetrations must ensure complete electrolyte and gas tightness even when positive plate is growing Fully insulated copper connectors and screw heads Interconnection lead poles with torque 20 - 22 Nm Communication ports: min. CAN 2.0, RS485, Bluetooth, (optional WiFi) Serial and parallel connections Energy efficiency > 80% Ampere-hour efficiency > 90% Self-discharge less than 2-3%/month at 20°C No memory effect Sufficiently large containers for electrolyte circulation The whole module is non-toxic, non-polluting, and environmentally friendly. Automatic battery module network connection, automatic IP addressing, easy maintenance, remote monitoring and update, support USB flash drives for firmware update. Each battery is labelled with at least the following data: Manufacturer, type, model number, nominal voltage in V, nominal capacity in Ah, month and year of commissioning.
| Charge regulator | Charge controller with MPPT technology. Maximum self-consumption 5 W. As hybrid system with charge regulator possible Complies with EN 62109-1. Electrical efficiency >90% (at 5 to 120% nominal power). Possibility to connect a remote control / remote monitoring is available Power supply for consumers (AC/DC) or battery charging via solar system or diesel generators (230 VAC) is possible Input voltage 230 V Protection class IP20
Supported battery types: Li-Ion Charge control: IUoU with automatic full and equalisation charging Protection of the battery against deep discharge, (current-dependent final discharge voltage) Protection of the battery against overcharging Regular equalisation charge (e.g. regular increase of the final charge voltage) Display of switch-off due to deep discharge and other reasons Battery voltage display (e.g. via LED) External battery temperature sensor included in the scope of delivery Low overvoltage with inductive and capacitive loads (please specify value) Permissibility of half-wave operation caused by power reduction with diode, e.g. hair dryer Compliance with EMC limits according to EN 50081 and EN 55014 ISO certification of the manufacturer is available
Protection functions: Short-circuit proof Overload protection Overtemperature protection Lightning and overvoltage protection AC side Compliance with other VDE/IEC regulations (contact protection etc.) Compliance with EMC limits (electromagnetic compatibility) according to EN 50081 and EN 55014 Radio interference suppression (VHF) Output power control of the feed-in inverter (item 1.3) via frequency for overcharge protection of the battery Other normative requirements IEC 62093 ;DIN EN 5178 ; are fulfilled CE declaration of conformity by the manufacturer is available and must be included with the offer. Confirmation by a conformity assessment body in accordance with ISO/IEC 17021 is available and must be included with the offer. CE marking of the battery-charging inverter is available. The battery charging inverters are marked accordingly. Communication point if necessary Control cable (e.g. LIYCY paired 2x2x0.25 or comparable type) if necessary
6 | Cable
| System cables | all neccessary connection cables for the battery system
| Data cable | Data cable to connect battery system with control unit
| Accessories | All accessories for proper fastening and installation of the battery systems.
9 | Documentation
| The following documentation, in English, must be supplied in electronic form for all components of the system after the order has been placed: | Assembly instructions for the entire system. Overview for an installer on site, showing which components are connected to each other and how. This overview also refers to the corresponding installation instructions and assembly instructions for the individual components.
Circuit document
Description of the components
Wiring diagrams
Assembly instructions, installation instructions
Commissioning instructions
Operating instructions
Maintenance instructions
Error analysis and troubleshooting suggestions in the event of a malfunction
10 | Delivery
| Delivery | All material must be delivered DDP German places latest 3 months after order. Each Battery System must be packed and marked singlely, always 3 systems needs to be deliverred to 1 destination. Expected destinations for deliveries are Aachen, Düsseldorf, Hamburg, Iserlohn, Kahl, Kassel, this destinations might change. Detailled addresses follows by giz with the order (3 systems each destination in Germany).
| Customs status | All goods must be EU Community goods or goods imported entirely into the EU. The bidder is responsible for import customs clearance into the EU, including all costs, duties and fees.
| Please specify: | Dimensions (LxWxH), weight (kg) incl. packaging for land shipment.
12 | Warranty
| min. 2 years | On the entire system and installation. Fully according to GIZ General Purchase Conditions 2023. This warranty takes precedence over product and manufacturer warranties. For individual components, longer warranty periods apply if described.
| Guarantee assignment declarations | All warranties must be assigned to GIZ and project partners by declaration. This declaration must be signed and stamped by each manufacturer.