## Specification
Lot | Position | Item description | Minimum Requirements | Quantity [total meters] | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns B-E, please indicate "Yes". Otherwise, describe your special features in this column. | Type of procedure | Source of price
1 | 1.1 | Pre-insulated PE steel pipe with leak alarm, 89/160 mm | Product type - pipe; pipe material - steel 20 (carbon content 0.17-0.24%); steel pipe diameter (external) - 89 mm; steel wall thickness - not less than 3.5 mm; preliminary thermal insulation - yes; thermal insulation material - polyurethane foam; polyethylene pipe diameter (external) - 160 mm; PE wall thickness - not less than 3.0 mm; pipe material - polyethylene (PE) not lower than PE 100; signaling - present; Pipe cutting length min. 9 m meeting the tab delivery plan; Execution according to DSTU B V.2.5-31:2007 or equivalent. | 162
| 1.2 | Pre-insulated PE steel pipe with leak alarm, 108/200 mm | Product type - pipe; pipe material - steel 20 (carbon content 0.17-0.24%); steel pipe diameter (external) - 108 mm; steel wall thickness - not less than 4.0 mm; preliminary thermal insulation - yes; thermal insulation material - polyurethane foam; polyethylene pipe diameter (external) - 200 mm; PE wall thickness - not less than 3.2 mm; cover pipe material - polyethylene (PE) not lower than PE 100; signaling - present; Pipe cutting length min. 9 m meeting the tab delivery plan; Execution according to DSTU B V.2.5-31:2007 or equivalent. | 300
| 1.3 | Pre-insulated PE steel pipe with leak alarm, 133/225 mm | Product type - pipe; pipe material - steel 20 (carbon content 0.17-0.24%); steel pipe diameter (external) - 133 mm; steel wall thickness - not less than 4.5 mm; preliminary thermal insulation - yes; thermal insulation material - polyurethane foam; polyethylene pipe diameter (external) - 225 mm; PE wall thickness - not less than 3.5 mm; cover pipe material - polyethylene (PE) not lower than PE 100; signaling - present; Pipe cutting length min. 9 m meeting the tab delivery plan; Execution according to DSTU B V.2.5-31:2007 or equivalent. | 120
| 1.4 | Pre-insulated PE steel pipe with leak alarm, 159/250 mm | Product type - pipe; pipe material - steel 20 (carbon content 0.17-0.24%); steel pipe diameter (external) - 159 mm; steel wall thickness - not less than 4.5 mm; preliminary thermal insulation - yes; thermal insulation material - polyurethane foam; polyethylene pipe diameter (external) - 250 mm; PE wall thickness - not less than 3.9 mm; cover pipe material - polyethylene (PE) not lower than PE 100; signaling - present; Pipe cutting length min. 9 m meeting the tab delivery plan; Execution according to DSTU B V.2.5-31:2007 or equivalent. | 2125
| 1.5 | Pre-insulated PE steel pipe with leak alarm, 219/315 mm | Product type - pipe; pipe material - steel 20 (carbon content 0.17-0.24%); steel pipe diameter (external) - 219 mm; steel wall thickness - not less than 6.0 mm; preliminary thermal insulation - yes; thermal insulation material - polyurethane foam; polyethylene pipe diameter (external) - 315 mm; PE wall thickness - not less than 4.9 mm; cover pipe material - polyethylene (PE) not lower than PE 100; signaling - present; Pipe cutting length min. 9 m meeting the tab delivery plan; Execution according to DSTU B V.2.5-31:2007 or equivalent. | 438
| 1.6 | Steel pipe, pre-insulated steel casing with leak alarm, 219/315 mm (SPIRO) | Product type - pipe; material of internal pipe - steel 20 (carbon content 0.17-0.24%); diameter of internal steel pipe (external) - 219 mm; steel wall thickness - not less than 6.0 mm; preliminary thermal insulation - yes; thermal insulation material - polyurethane foam; diameter of protective steel pipe (external) - 315 mm; thickness of steel wall (protective pipe) - not less than 0.6 mm; material of protective pipe - metal resistant to atmospheric corrosion, or with an appropriate anti-corrosion coating; alarm - present; Pipe cutting length min. 9 m meeting the tab delivery plan; Execution according to DSTU B V.2.5-31:2007 or equivalent. | 50
| 1.7 | Pre-insulated PE steel pipe with leak alarm, 273/400 mm | Product type - pipe; pipe material - steel 20 (carbon content 0.17-0.24%); steel pipe diameter (external) - 273 mm; steel wall thickness - not less than 7.0 mm; preliminary thermal insulation - yes; thermal insulation material - polyurethane foam; polyethylene pipe diameter (external) - 400 mm; PE wall thickness - not less than 6.3 mm; cover pipe material - polyethylene (PE) not lower than PE 100; signaling - present; Pipe cutting length min. 9 m meeting the tab delivery plan; Execution according to DSTU B V.2.5-31:2007 or equivalent. | 144
2 | 2.1 | Electric-welded steel pipe, 57 mm | Product type - electric welded pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 57 mm; steel wall thickness - not less than 3 mm; execution according to DSTU 8943:2019 or equivalent. | 200
| 2.2 | Electric-welded steel pipe, 76 mm | Product type - electric welded pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 76 mm; steel wall thickness - not less than 3.5 mm; execution according to DSTU 8943:2019 or equivalent. | 200
| 2.3 | Electric-welded steel pipe, 89 mm | Product type - electric welded pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 89 mm; steel wall thickness - not less than 3.5 mm; execution according to DSTU 8943:2019 or equivalent. | 200
| 2.4 | Electric-welded steel pipe, 108 mm | Product type - electric welded pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 108 mm; steel wall thickness - not less than 4 mm; execution according to DSTU 8943:2019 or equivalent. | 100
| 2.5 | Electric-welded steel pipe, 159 mm | Product type - electric welded pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 159 mm; steel wall thickness - not less than 4.5 mm; execution according to DSTU 8943:2019 or equivalent. | 100
| 2.6 | Electric-welded steel pipe, 219 mm | Product type - electric welded pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 219 mm; steel wall thickness - not less than 6 mm; execution according to DSTU 8943:2019 or equivalent. | 60
| 2.7 | Electric-welded steel pipe, 426 mm | Product type - electric welded pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 426 mm; steel wall thickness - not less than 6 mm; execution according to DSTU 8943:2019 or equivalent. | 6
3 | 3.1 | Seamless hot-deformed steel pipe, 42 mm | Product type - seamless hot-deformed pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 42 mm; steel wall thickness - not less than 3.5 mm; execution according to DSTU 8938:2019 or equivalent. | 300
| 3.2 | Seamless hot-deformed steel pipe, 57 mm | Product type - seamless hot-deformed pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 57 mm; steel wall thickness - not less than 4 mm; execution according to DSTU 8938:2019 or equivalent. | 1000
| 3.3 | Seamless hot-deformed steel pipe, 76 mm | Product type - seamless hot-deformed pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 76 mm; steel wall thickness - not less than 5 mm; execution according to DSTU 8938:2019 or equivalent. | 600
| 3.4 | Seamless hot-deformed steel pipe, 89 mm | Product type - seamless hot-deformed pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 89 mm; steel wall thickness - not less than 5.0 mm; execution according to DSTU 8938:2019 or equivalent. | 600
| 3.5 | Seamless hot-deformed steel pipe, 530 mm | Product type - seamless hot-deformed pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 530 mm; steel wall thickness - not less than 10 mm; execution according to DSTU 8938:2019 or equivalent. | 250
| 3.6 | Electric-welded steel pipe, 530 mm | Product type - electric welded pipe; pipe material - steel 20 (carbon content 0.17-0.24%); pipe diameter (external) - 530 mm; steel wall thickness - not less than 10 mm; execution according to DSTU 8943:2019 or equivalent. | 600
4 | 4.1 | Polypropylene pipe, 63 mm | Product type - pipe; shape - straight; pipe material - polypropylene; reinforcement type - with reinforcement; outer diameter - 63 mm; wall thickness - not less than 10.5 mm; maximum working pressure - 20 bar; maximum working temperature - +90°C; working medium - hot water; DSTU EN ISO 15874-3:2022 / ISO/CD 15874-3 or equivalent. | 1450
| 4.2 | Polypropylene pipe, 40 mm | Product type - pipe; shape - straight; pipe material - polypropylene; reinforcement type - with reinforcement; outer diameter - 40 mm; wall thickness - not less than 6.7 mm; maximum working pressure - 20 bar; maximum working temperature - +90°C; working medium - hot water; DSTU EN ISO 15874-3:2022 / ISO/CD 15874-3 or equivalent. | 1200
| 4.3 | Polypropylene pipe, 32 mm | Product type - pipe; shape - straight; pipe material - polypropylene; reinforcement type - with reinforcement; outer diameter - 32 mm; wall thickness - not less than 5.4 mm; maximum working pressure - 20 bar; maximum working temperature - +90°C; working medium - hot water; DSTU EN ISO 15874-3:2022 / ISO/CD 15874-3 or equivalent. | 1600

## Delivery Plan
No. | Delivery address | Position
| The delivery schedule contains only the location details. A detailed address will be provided for each location after order. | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 2.10 | 2.11 | 2.12 | 2.13 | 3.1 | 3.2 | 3.3
1 | Smila | Position 1.2: 300; Position 1.4: 400; Position 1.5: 60
2 | Monastyrysche | Position 1.4: 150
3 | Kyiv | Position 1.1: 162; Position 1.4: 1080; Position 1.5: 63; Position 1.7: 144
4 | Boryspil | Position 1.5: 290
5 | Bila Tserkva | Position 1.5: 25; Position 1.6: 50
6 | Pavlograd | Position 1.4: 495
7 | Kamyanske | Position 2.8: 300; Position 2.9: 1000; Position 2.10: 600; Position 2.11: 600; Position 2.12: 250
8 | Pryluky | Position 2.1: 100; Position 2.2: 100; Position 2.3: 100; Position 2.4: 100; Position 2.5: 100; Position 2.6: 60; Position 2.7: 6
9 | Chernihiv TKE | Position 2.13: 600
10 | Sumy | Position 2.1: 100; Position 2.2: 100; Position 2.3: 100; Position 3.1: 1450; Position 3.2: 1200; Position 3.3: 1600
11 | Novovolynsk | Position 1.3: 120
| Total qty | 162 | 300 | 120 | 2125 | 438 | 50 | 144 | 200 | 200 | 200 | 100 | 100 | 60 | 6 | 300 | 1000 | 600 | 600 | 250 | 600 | 1450 | 1200 | 1600

## Dropdown menu (hidden)
Type of Equipment |  | please choose
Notebook |  | Yes
PC |  | No
Accesorities | (Mouse, Keyboard, Docking Station..)
Office technic | Telephone,MFD, printer
Network components | Router, switch, UPS
Cartridge |  | Justification for non-neutral specification
Licence, Software |  | please choose
Monitor |  | Special manufacturing
TV |  | Compatibility/Standartization in the Project/ Partner organisation
Spare parts/ Aditional equipment/ accessories only by one Supplier
Maintenance
Category of good:
please choose
S01 Food, beverages, tobacco products
S02 Computer system
S03 Telecommunications device
S04 Standard Software rent (goods)
S05 Standard Software buy (goods)
S06 Plant Equipment, tool
S07 Construction technology
S08 Office product, facility and technic, papeterie
S09 Literature
S10 Hardware rent
S11 Energy, extraction product, secondary raw material, residue
S12 Electric engineering, automation, process control engineering
S13 Vehicle (complete vehicle)
S14 Home economics, Home technology
S15 Laboratory material, laboratory technology
S16 Installation (complete)
S17 Medical device
S18 Machine, apparatus
S19 Occupational safety, accident prevention
S20 Marketing
S21 Automotive engineering, vehicle component
S22 Human and veterinary drug, pesticide, active ingredient
S23 Clothing and textiles
S24 Body care, personal hygiene
S25 Sport, playing, leisure
S26 Interior furnishing (excl. Office furnishings)